3.2	Installation of a New U5 Rack Frame


Confirm the following before newly installing or moving the rack frame.


Notice :	Securely close the front door, the rear door, and the side covers of the rack frame for safety when installing or moving the rack frame.





�
Reception of the rack frame�
�
�
�
�
�
�
�
�
Work (�
Installation of the rack frame�
�
�
�
��
(1) Removing of the Side Panel and Skirt(S)�
�
See FR-INS-0210�
�
��
(2) Adhering the GASKETs�
�
See FR-INS-0220�
�
��
(3) Connection�
�
See FR-INS-0230�
�
��
(4) Installing of the Side Panel and Skirt(S)�
�
See FR-INS-0250�
�
��
(5) Installing the skirts�
�
See FR-INS-0260�
�
�
�
�
�
�
Work (�
Connection of the rack frame�
�
�
�
��
(1) Connecting the power cables�
�
See FR-INS-0270�
�
��
(2) Connecting the I/F cables�
�
See FR-INS-0280�
�
Tools listed below are required for the installation.





3.2.1	Tools required


Table 3.2.1  Tools Required


No.�
Tool name�
Specification�
Usage�
�
1�
Spanner�
No.24�
Adjusting the leveling bolts.�
�
2�
Spanner�
No.13�
For connection of the side cover and frame.�
�
3�
Phillips screwdriver�
No.2�
Attaching the skirts.�
�
4�
Hexagon wrench�
No.6�
Opening and closing the doors.�
�






�
3.2.2	Inspecting all the components visually


Check the following components before installation according to a customer’s configuration.


Table 3.2.2  Mandatory Features


No.�
Parts No.�
Model Name�
Specification�
Quantity�
Comment�
�
1�
5501839-B�
DF-F400-U5�
Rack frame. (U5)�
1�
�
�
2�
3255104-1�
SKIRT (F/R)�
For front and rear.�
2�
�
�
3�
5411531-2�
SCREW (BLACK)�
For skirt.�
6�
�
�
4�
5501745-1�
GASKET�
For rack frame. (right-hand side)�
2�
�
�
5�
5501745-2�
�
�
2�
�
�
6�
5501745-41�
�
�
6�
�
�
7�
5501745-42�
�
�
2�
�
�
8�
BH871�
BOLT�
For connecting.�
8�
�
�
9�
WS008�
SPRING WASHER�
For connecting�
8�
�
�
10�
WP008�
WASHER�
For connecting�
16�
�
�
11�
NF008�
NUT�
For connecting�
12�
�
�
12�
SB510�
BIND SCREW�
For grand cable.�
2�
�
�
13�
WS005�
SPRING WASHER�
�
2�
�
�
14�
WP005�
WASHER�
�
2�
�
�
15�
3255162-E�
CABLE (VRC)�
Remote cable (P200-0)�
1�
�
�
16�
3255162-F�
CABLE (VRC)�
Remote cable (P200-1)�
1�
�
�



3.2.3	Unpacking


(1)	Unpacking the U5 rack frame.





3.2.4	Installation


Make sure of the following before starting the installation.


(	The site for installation must be flat.


(	Gently position the side frames making them adjoin each other.  When positioning them, take care not to drop their casters into cutouts on the floor nor to hit their corners. (When cables protrude from the floor, take special care to avoid them.


(	To align the rack frames, use their front sides as the reference planes.











�
(1)	Removing the side panel and skirt (side) of the CPU frame


In order to connect the host and the U5, remove the side panel, side hook, and skirt on the left side of the CPU frame.  Those parts are to be installed on the terminal U5 later (see step (4)).


Tools required : Philips screwdriver (No.2)�Spanner (No.13)


(a)	Open the front and rear doors of the CPU frame.


(b)	Remove the side panel and the grand cables.


(c)	Remove eight bolts (bolt M8(36) fastening the side panel of the CPU frame.


(d)	Remove two screws ( fastening each of the two side focks of the CPU frame.


(e)	Remove three screws( fastening the skirt (side) of the CPU frame.





� EMBED Word.Picture.6  ���





Figure 3.2.1  Removeing of the Side Cover and Skirt


�
(2)	Adhering the GASKETs


Adhier the GASKETs on the joining side (right-hand side) of the U5 rack frame before connecting the frames.  When adhering the GASKETs, position them so that their holes are aligned with those on the rack frame.�for types and adhering positions of the GASKETs, see Figure 3.2.2 below.





� EMBED Word.Picture.6  ���





Figure 3.2.2  Types and Adhering Positions of GASKET





�
(3)	Connection


(a)	Adjusting height and tilt


Before connecting the frames, align the U5 rack frames and adjust their heights and tilts by turning the leveling bolts.


(i)	Make the heights of the rack frames even.�When adjusting the heights, aim at making each gap between the caster and the floor 2.5 mm.





� EMBED Word.Picture.6  ���





Figure 3.2.3  Inclination of Rack Frame





(ii)	Adjust the tilt of the each rack frame within the allowable limit.





� EMBED Word.Picture.6  ���





Figure 3.2.4  Space between Caster and Floor


�
(b)	Connecting the frames


(i)	Place the U5 rack frames at the position for connection. (See Figure 3.2.5)


(ii)	Open the front and rear doors. (See page FR-REP-0140).


(iii)	Connect the rack frames adjacent each other by fastening them with the bolts (eight each) supplied with the rack frames.  (See Figure 3.2.5)


(iv)	Connect the grounding cables (two cables front and rear for each set of adjoining rack frames) with the M5(10 binding screws. (See Figure 3.2.6.)


� EMBED Word.Picture.6  ���


Figure 3.2.5  How to Connect the Rack Frames


DF400	K6601945-





REV.0�
Jan.1999�
�
�
�
�
�
�
Copyright ( 1999, Hitachi, Ltd.


FR-INS-0190





REV.1�
Jan.1999�
Aug.1999�
�
�
�
�
�
Copyright ( 1999, Hitachi, Ltd.


FR-INS-0200





REV.0�
Jan.1999�
�
�
�
�
�
�
Copyright ( 1999, Hitachi, Ltd.


FR-INS-0210





REV.0�
Jan.1999�
�
�
�
�
�
�
Copyright ( 1999, Hitachi, Ltd.


FR-INS-0220





REV.0�
Jan.1999�
�
�
�
�
�
�
Copyright ( 1999, Hitachi, Ltd.


FR-INS-0230





REV.0�
Jan.1999�
�
�
�
�
�
�
Copyright ( 1999, Hitachi, Ltd.


FR-INS-0240











