5.4	Cable routing


Notice :	Start the work after referring to notes on cable routing given on page ENT-0081 in Chapter 2, “ENTRY”.


5.4.1	Connecting the power cables/remote cables of the mounted subsystem


(1)	Confirm that the circuit breaker (CB1) of the PDBs (PDB 0, 1) corresponding to the mounted unit has been turned off.


(2)	Insert each power cable plug into the receptacle on the IN BOX of the mounted unit.


(3)	Insert the plug at the opposite end to that of the each power cable mentioned in step (2) into the outlet of the PDB. (See Table 5.4.1)


(4)	Insert each remote cable plug into the receptacle on the IN BOX of the mounted unit.


(5)	Insert the plug at the opposite end to that of the each remote cable mentioned in step (2) into the outlet of the PDB. (See Table 5.4.1)





� EMBED Word.Picture.6  ���





Figure 5.4.1  Routing the Power Cables


Notice :	(1)	Be sure to plug the power cable for the IN BOX 00 in the outlet of the PDB 0.�Be sure to plug the power cable for the IN BOX 01 in the outlet of the PDB 1.�If they are plugged in the outlets of the same PDB or reversed, the function of the duplicated power supply does not work.


(2)	Do not plug any cable other than the power cable of the mounted RK type subsystem in the outlet of the PDB.


�



� EMBED Word.Picture.6  ���


Figure 5.4.2  Appearance of PDB


� EMBED Word.Picture.6  ���


A large leak current flows when plural subsystems of DF400-RK are installed. Be sure to ground them for preventing an electric shock accident.





Table 5.4.1  Connect the cable plug


IN BOX�
Cable plug label�
PDB�
�
Connector�
IN BOX side�
PDB side�
Connect label�
�
Power cable�
J110-0 (IN BOX 00 of the lower


RK type subsystem)�
P110-0�
P10-0�
J10-0 (Connect for J10 of lower


PDB0.)�
�
�
J110-1 (IN BOX 01 of the lower


RK type subsystem)�
P110-1�
P10-1�
J10-1 (Connect for J10 of upper


PDB1.)�
�
�
J111-0 (IN BOX 00 of the upper


RK type subsystem)�
P111-0�
P11-0�
J11-0 (Connect for J11 of lower


PDB0.)�
�
�
J111-1 (IN BOX 01 of the upper


RK type subsystem)�
P111-1�
P11-1�
J11-1 (Connect for J11 of upper


PDB1.)�
�
Remote cable�
J210-0 (IN BOX 00 of the lower


RK type subsystem)�
P210-0�
P100-0�
J100-0 (Connect for J100-0 of


lower PDB0.)�
�
�
J210-1 (IN BOX 01 of the lower


RK type subsystem)�
P210-1�
P100-1�
J100-1 (Connect for J100-1 of


upper PDB1.)�
�
�
J211-0 (IN BOX 00 of the upper


RK type subsystem)�
P211-0�
P101-0�
J101-0 (Connect for J101-0 of


lower PDB0.)�
�
�
J211-1 (IN BOX 01 of the upper


RK type subsystem)�
P211-1�
P101-1�
J101-1 (Connect for J101-1 of


upper PDB1.)�
�



�
5.4.2	Connecting the panel junction cables


(1)	Connect the junction cable connectors (P10 and P11) to the connectors (J10 and J11) of the subsystems in the order from bottom to top.


� EMBED Word.Picture.6  ���


Figure 5.4.3  Connection of Junction Cables (Rear Side)


Table 5.4.2  Connect the Junction Cables


(Front of subsystem)�
Jnction cable plug label�
(Rear of subsystem)�
�
SH187 PK ASSY


connector�
SH187 PK ASSY side�
SVP ASSY side�
SVP ASSY connector of RK type subsystem�
�
J100�
P100�
P10�
J10 (Connect for lower mounted of


RK type subsystem)�
�
J101�
P101�
P11�
J11 (Connect for upper mounted of


RK type subsystem)�
�



�
(2)	Connect the plugs of the junction cables to socket connectors (J100 and J101) of the SH187 PK ASSY.





� EMBED Word.Picture.6  ���





Figure 5.4.4  Connection of Junction Cables (Front Side)





�
5.4.3	Routing the interface cables of the mounted subsystem


Start the work after referring to notes on cable routing given on page ENT-0081 in Chapter 2, “ENTRY”.


(1)	Routing the interface cables


�Notice :	When bending the Fibre Channel cable to connect it, give it a bend with a long radius (not less than 30mm) so as not to apply the cable and the connector an excessive stress.


(a)	Pass the I/F cable through an opening for the external connection cables on the bottom of the rack frame, and pull it into the frame.


(b)	Connect the I/F cable to the specified connector of the I/F ADAPTER ASSY.


(c)	Clamp the I/F cable with a locking wire saddle, and route it.   When doing this, give the cable excess length to allow components to be replaced.   Besides, be careful not to bend the cable sharply.





(2)	Routing the remote cables


(a)	Remove the cable over by loosening two screws (SB408s).


(b)	Loosen an installed Repeat Binder, pass the remote cable through the cable duct and the hole for the remote cable, and connect it ito the PDB (J200-0/F200-1).


(c)	Fasten the remote cable with Repeat Binders.


(d)	Reinstall the cable cover.








�



� EMBED Word.Picture.6  ���





Figure 5.4.5  Routing the I/F Cables





�
6.	Procedures for Adding UPS or Additional Battery Unit on the U4 Rack Frame


Add the UPS or the additional battery unit on the rack frame referring to the following:


( Related manual�“Disk Subsystem UPS manual”�“Disk Subsystem UPS MANUAL Mounting on Rack Frame” (See Chapter 2)











DF400	K6601946-





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-OPT-0540





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-OPT-0550





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-OPT-0560





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-OPT-0570





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-OPT-0580





Copyright © 1999, Hitachi, Ltd.


REV.0�
Aug.1999�
�
�
�
�
�
�
FR-OPT-0585





Copyright © 1999, Hitachi, Ltd.


REV.0�
Jun.1999�
�
�
�
�
�
�
FR-OPT-0590








Fibre Channel cable





R





I/F ADAPTER ASSY











