3.	Installing the UPS Into HP Rack Frame


Installing the UPS on the rack frame referring to the following:


( Related manual�“Disk Subsystem UPS manual”�“Disk Subsystem UPS MANUAL Mounting on Rack Frame” (See Chapter 2)





�
4.	Mounting UPDU on HP Rack Frame


4.1	Height of Required Space in Rack Frame


The height of the space required for mounting the UPDU on the HP rack frame is one unit of the EIA standard.


4.2	Optional Parts for Mounting (Model Name : DF-F400-UPDU)


(	The optional parts and their quantities required to mount the one UPDU are shown below.


Table 4.2.1  Composition of DF-F400-UPDU (per UPDU)


No.�
Part No.�
Part Name�
Qty.�
Remarks�
�
�
1�
5500750-12�
PDU�
1�
PDU (C13×6L, C19×2)�
�
�
2�
5500750-13�
Power cable�
1�
L6-30P 4.5 m�
�
�
3�
5490841-20�
Cage nut (For GND)�
3�
(Not used)�
�
�
4�
5490841-13�
Washer (For GND)�
6�
For securing the PDU


(2 spare is included)�
�
�
5�
SB416�
Bind screw (M4 × 16)�
3�
(Not used)�
�
�
6�
SB516�
Bind screw (M5 × 16)�
�
For securing the PDU


(1 spare is included)�
�
�
7�
NF005�
Nut (M5)�
3�
For securing the PDU


(1 spare is included)�
�
�
8�
2051001-413�
LL washer�
3�
(Not used)�
�
�
9�
3243319-232�
Name plate�
�
Already affixed to PDU�
�
�



4.3	Tool Required


(	Phillips screwdriver (No.1, No.2)


(	Wrench (nominal size : 8 × 10)


(	Torque wrench (T25) *1


*1 : Used to remove parts previously installed in the HP frame.








�
4.4	Installing UPDU in Rack Frame


Notice :	Install the PDU making it face the rear of the rack frame.


(1)	Align each mounting hole of the PDU with the hole on each pillar of the rack frame located at the center of the position for mounting the unit.


(2)	Fasten the PDU with binding screws (M5 × 10), nuts (M5) and washers. (Take care not to mistake an orientation of the washer ) 





� EMBED Word.Picture.6  ���








Figure 4.4.1  Installing the UPDU


�
4.5  Connecting power cables


(1)	Remove the screws ( and reorient it, when necessary, so that you can handle it easily. ( See Figure 4.5.1.)


(2)	Loosen the screw ( and insert the power cable into the strain relife ( See Figure 4.5.1.) (*1)


(3)	Tighten the screws ( and fasten the power cable. 





� EMBED Word.Picture.6  ���





Figure 4.5.1  Connecting the Power Cable





*1	If you cannot insert the power cable easily even when the screw ( is loosened, do as shown below. 


(1)	Remove the screws ( and remove the strain relief. 


(2)	Remove the screw ( and attach the strain relief to the power cable. (See Figure 4.5.2.)


(3)	Insert the power cable into the PDU, and then fasten the strain relief. (See Figure 4.5.3.) 


(4)	Tighten the screws ( and fasten the power cable. 








� EMBED Word.Picture.6  ���


Figure 4.5.2  Installing the Strain Relief      Figure 4.5.3  Connecting the Power Cable 





DF400	K6601645-





Copyright © 1999, Hitachi, Ltd.


REV.0�
Jun.1999�
�
�
�
�
�
�
FR-HP-0240





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-HP-0250





Copyright © 1999, Hitachi, Ltd.


REV.1�
Jun.1999�
Aug.1999�
�
�
�
�
�
FR-HP-0260





Copyright © 1999, Hitachi, Ltd.


REV.0�
Aug.1999�
�
�
�
�
�
�
FR-HP-0270














