4.2 Disconnection of External Cable

4.2.1 Disconnection of AC Cable

4.2.1.1 DKC210IU/DKU205IU



� DANGER

The DKC and the first DKU commonly have Two Main Disconnect Devices (Two Main Breaker CB101s for Dual Power Lines) so that AC Power of the unit can be supplied from the separate power distribution board with Two Power Supply Cords.  Similarly, each of the 2nd DKU, the 3rd DKU and, the 4th DKU also has Two Main Disconnect Devices.

Observe all instructions described in this manual before connecting the equipment to the power source and before servicing.



A.	Connection of Power Supply Cord

	The unit has two power supply cords with attachment plug type R&S 3760 or 3760PDG.  Be sure to prepare the following socket receptacles and power cords between the power distribution board of the building and the attachment plugs for the unit.



	Socket Receptacle :  R&S 3754 or 3934

	Power Cord :  Type ST or equivalent, shielded type, with four min. #8 AWG conductors. Terminated at one end with an assembled on above socket receptacle cap.



B.	Requirements to Branch Circuit

	This unit relies on the building installation for protection of the internal components of the equipment.  Each line (R/S/T line) should be protected by a short circuit protective device and by an overcurrent protective device rated 30 amp on building installation.

	The protective device on building installation shall comply with the NEC requirements (or CEC requirements when installed in Canada), and if a protective device interrupts a conductor, it shall also interrupt all other supply conductors.

	This protection is not required for the neutral line of this unit.



C.	Disconnection from Power Supply

	Each unit has Two Main Disconnect Device (Two Main Breaker CB101s for Dual Power Lines).

	To remove all utility power from the unit, turn off both main disconnect device CB101s at the same time.





�a.	Refer to Fig. 4.2-1.  Disconnect the AC cables.



�EMBED MSDraw  \* MERGEFORMAT���



Fig. 4.2-1  Disconnection of the AC cables



�4.2.1.2 DKC210IE/DKU205IE



� DANGER

The DKC and the first DKU commonly have Two Main Disconnect Devices (Two Main Breaker CB101s for Dual Power Lines) so that AC Power of the unit can be supplied from the separate power distribution board with Two Power Supply Cords.  Similarly, each of the 2nd DKU, the 3rd DKU, and the 4th DKU also has Two Main Disconnect Devices.

Observe all instructions described in this manual before connecting the equipment to the power source and before servicing.



A.	Connection of Power Supply Cord

	The unit has two power supply cords.  Be sure to prepare the following socket receptacles and power cords between the power distribution board of the building and the power cords for the unit.



	Socket Receptacle :  As shown in the following figure.

	Power Cord :  Type H07RN-F or equivalent, with five 6.0 mm 2 conductors. Terminated at one end with an assembled on above socket receptacle cap.



	Be sure to connect a power cord to the distribution box as illustrated in the following figure.  The wrong connection of neutral line may cause damages or fire of the equipment.

	To reduce the risk of wrong connection, you should use approved type attachment plug and socket for power cord connection.

	High leakage current may be caused between the power supply and this unit.  To avoid an electric shock by high leakage current, perform the protective earth connection before the supply connections and disconnect it after the supply connections.



B.	Requirements to Branch Circuit

	This unit relies on the building installation for protection of the internal components of the equipment.  Each line (R/S/T line) should be protected by a short circuit protective device and by an overcurrent protective device rated 30 amp on building installation.

	The protective device on building installation shall be comply with National Standards of the country where the units shall be installed, and if a protective device interrupts a conductor, it shall also interrupt all other supply conductors.

	This protection is also required for the neutral line of this unit.



C.	Disconnection from Power Supply

	Each unit has Two Main Disconnect Device (Two Main Breaker CB101s for Dual Power Lines).

	To remove all utility power from the unit, turn off both main disconnect device CB101s at the same time.



�a.	Refer to Fig. 4.2-2.  Disconnect the AC cables.



�EMBED MSDraw  \* MERGEFORMAT���

Fig. 1.4.2-2  Disconnection of the AC cables



�4.2.2 Disconnection of Channel Interface Cable

4.2.2.1 Disconnection of Parallel Channel Interface Cable

a.	Refer to Fig. 4.2-3.  Disconnect the Parallel Channel Interface cables.

�EMBED MSDraw  \* MERGEFORMAT���

Fig. 4.2-3  Disconnection of the Parallel Channel Interface cables



4.2.2.2 Disconnection of Serial Channel Interface Cable

a.	Refer to Fig. 4.2-4.  Disconnect the Serial Channel Interface cables.

�EMBED MSDraw  \* MERGEFORMAT���

Fig. 4.2-4  Disconnection of the Serial Channel Interface cable



�4.2.2.3 SCSI Channel Interface Cable

a.	refer to Fig. 4.2-5.  Disconnect the SCSI Channel Interface cables.



�EMBED MSDraw  \* MERGEFORMAT \s���

Fig. 4.2-5  Disconnection of the SCSI Channel Interface cables





�4.2.3 Disconnection of PCI Cable

a.	Refer to Fig. 4.2-6.  Disconnect the PCI cables.

�EMBED MSDraw  \* MERGEFORMAT���

Fig. 4.2-6  Disconnection of the PCI cables



4.2.4 Disconnection of RCU Cable

a.	Refer to Fig. 4.2-7.  Disconnect the RCU cables.

�EMBED MSDraw  \* MERGEFORMAT���

Fig. 4.2-7  Disconnection of the RCU cables



	K6601527-



REV.0�Jun.1998�������Copyright ©1998, Hitachi, Ltd.

DKCREP04-�page �6�0










