4.4.2 Connection between DKC and Second DKU





(1)  Loosen the repeat binders which secure the SCSI interface cables for the Disk Controller.





� EMBED Word.Picture.6  ���


Fig. 4.4.2-1 Loose of repeat binders





(2)	Pass the SCSI interface cables for the Disk Controller through the second DKU frame.  Be extremely careful not to pinch the inter-frame cable when coupling the frames to each other.





Notice :	Move the DKC and the DKU as being careful of floor cut.





� EMBED Word.Picture.6  ���





Fig. 4.4.2-2  Attachment of the second DKU





�
(3)  Install the Second DKU.


a.	Lower the screw jacks until the frame is 57 mm (2.25 in.) from the floor before connecting the frames.


b.	Level the device as shown on Fig. 4.4.2-3.


c.	When adjusting the cabinet height, make sure that there is a clearance of approximately 2.5 mm (0.1 in.) between the casters and the floor.





� EMBED Word.Picture.6  ���


� EMBED Word.Picture.6  ���


� EMBED Word.Picture.6  ���


Fig. 4.4.2-3  Cabinet Setting





�
(4)  Connect the connecting bolt.


a.	Loosen the four screws (M3) and the two screws (M4), remove the Front Logic Box Cover from the Disk Controller Unit.


b.	Loosen the two screws (M3) and remove the cover (frame) 4.


� EMBED Word.Picture.6  ���


Fig. 4.4.2-4  Removal of Covers (DKC front side)





c.	Loosen the four screws (M3) and the two screws (M4), remove the Rear Logic Box Cover.


d.	Loosen the two screws (M3) and remove the cover (frame) 1.


� EMBED Word.Picture.6  ���


Fig. 4.4.2-5  Removal of Covers (DKC rear side)





�
e.	Connect the devices together using six of Connecting Bolt assemblies, three in front and three in rear.


� EMBED Word.Picture.6  ���


� EMBED Word.Picture.6  ���


Fig. 4.4.2-6  Connection of Frame





�
(5)  Secure the power cable assy.


a.	Loose the four screws.





� EMBED Word.Picture.6  ���� EMBED Word.Picture.6  ���


Fig. 4.4.2-7  Fixing of the power cable assy





b.	Secure the power cable assy with screws.





� EMBED Word.Picture.6  ���� EMBED Word.Picture.6  ���


Fig. 4.4.2-8  Fixing of the power cable assy





�
(6)  Attach the frame ground cable.





� EMBED Word.Picture.6  ���


Fig. 4.4.2-9  Attachment of Frame Ground Cable





(7)  Secure the kick plates with screws.





Notice :	Contact the Kick Plate to the floor to prevent static electricity.


a.	In case that there is second DKU.


� EMBED Word.Picture.6  ���


Fig. 4.4.2-10  Installation of Kick Plate (Two DKUs)





�
b.	In case that there is third DKU.


� EMBED Word.Picture.6  ���


Fig. 4.4.2-11  Installation of Kick Plate (Three DKUs)





c.	In case that there is fourth DKU.


� EMBED Word.Picture.6  ���


Fig. 4.4.2-12  Installation of Kick Plate (Four DKUs)





�
(8)  Bind the DKUMN cables with repeat binders.


a.	Loosen the screws.


b.	Lift the DKUMN PCB.


c.	Slide and secure the DKUMN PCB.


� EMBED Word.Picture.6  ���


Fig. 4.4.2-13  Lift of DKUMN PCBs





d.	Bind the DKUMN cables with repeat binders.





� EMBED Word.Picture.6  ���





� EMBED Word.Picture.6  ���


Fig. 4.4.2-14  Binding of DKUMN cables





�
(9)  Bind the SCSI interface cables.


a.	Bind the SCSI interface cables with cable fixing wires and repeat binders.





� EMBED Word.Picture.6  ���





� EMBED Word.Picture.6  ���


Fig. 4.4.2-15  Binding of SCSI interface cables











	K6601527-





REV.0�
Jun.1998�
�
�
�
�
�
�
Copyright ©1998, Hitachi, Ltd.


DKCREP04-�page �47�0














