4.5 Connection of External Cable


4.5.1 Connection of AC Cable


4.5.1.1 DKC310IU/DKU205IU





� DANGER


	The DKC and the first DKU commonly have Two Main Disconnect Devices (Two Main Breaker CB101s for Dual Power Lines) so that AC Power of the unit can be supplied from the separate power distribution board with Two Power Supply Cords.  Similarly, each of the 2nd DKU, the 3rd DKU and, the 4th DKU also has Two Main Disconnect Devices.


	Observe all instructions described in this manual before connecting the equipment to the power source and before servicing.





A.	Connection of Power Supply Cord


	The unit has two power supply cords with attachment plug type R&S 3760 or 3760PDG.  Be sure to prepare the following socket receptacles and power cords between the power distribution board of the building and the attachment plugs for the unit.





	Socket Receptacle :  R&S 3754 or 3934


	Power Cord :  Type ST or equivalent, shielded type, with four min. #8 AWG conductors. Terminated at one end with an assembled on above socket receptacle cap.





B.	Requirements to Branch Circuit


	This unit relies on the building installation for protection of the internal components of the equipment.  Each line (R/S/T line) should be protected by a short circuit protective device and by an overcurrent protective device rated 30 amp on building installation.


	The protective device on building installation shall comply with the NEC requirements (or CEC requirements when installed in Canada), and if a protective device interrupts a conductor, it shall also interrupt all other supply conductors.


	This protection is not required for the neutral line of this unit.





C.	Disconnection from Power Supply


	Each unit has Two Main Disconnect Device (Two Main Breaker CB101s for Dual Power Lines).


	To remove all utility power from the unit, turn off both main disconnect device CB101s at the same time.





�
a.	Refer to Fig. 4.5-1.  Connect the AC cables.





� EMBED Word.Picture.6  ���





Fig. 4.5-1  Connection of the AC cables





�
4.5.1.2 DKC310IE/DKU205IE





� DANGER


	The DKC and the first DKU commonly have Two Main Disconnect Devices (Two Main Breaker CB101s for Dual Power Lines) so that AC Power of the unit can be supplied from the separate power distribution board with Two Power Supply Cords.  Similarly, each of the 2nd DKU, the 3rd DKU, and the 4th DKU also has Two Main Disconnect Devices.


	Observe all instructions described in this manual before connecting the equipment to the power source and before servicing.





A.	Connection of Power Supply Cord


	The unit has two power supply cords.  Be sure to prepare the following socket receptacles and power cords between the power distribution board of the building and the power cords for the unit.





	Socket Receptacle :  As shown in the following figure.


	Power Cord :  Type H07RN-F or equivalent, with five 6.0 mm 2 conductors.  Terminated at one end with an assembled on above socket receptacle cap.





	Be sure to connect a power cord to the distribution box as illustrated in the following figure.  The wrong connection of neutral line may cause damages or fire of the equipment.


	To reduce the risk of wrong connection, you should use approved type attachment plug and socket for power cord connection.


	High leakage current may be caused between the power supply and this unit.  To avoid an electric shock by high leakage current, perform the protective earth connection before the supply connections and disconnect it after the supply connections.





B.	Requirements to Branch Circuit


	This unit relies on the building installation for protection of the internal components of the equipment.  Each line (R/S/T line) should be protected by a short circuit protective device and by an overcurrent protective device rated 30 amp on building installation.


	The protective device on building installation shall be comply with National Standards of the country where the units shall be installed, and if a protective device interrupts a conductor, it shall also interrupt all other supply conductors.


	This protection is also required for the neutral line of this unit.





C.	Disconnection from Power Supply


	Each unit has Two Main Disconnect Device (Two Main Breaker CB101s for Dual Power Lines).


	To remove all utility power from the unit, turn off both main disconnect device CB101s at the same time.





�
a.	Refer to Fig. 4.5-2.  Connect the AC cables.





� EMBED Word.Picture.6  ���








Fig. 4.5-2  Connection of the AC cables





�
4.5.2 Connection of Channel Interface Cable


Table 4.5.2-1 shows the mounting limitations of channel options and the corresponding interface connector panel locations.


� EMBED Word.Picture.6  ���


Table 1.4.5.2-1  The Mounting Limitation of Channel Options


Case�
Location�
Number of�
I/F Connector Panel Location and Channel No.�
�
�
Basic�
Add.1�
Add.2�
Add.3�
Channel Ports�
Front View of DKC�
Rear View of DKC�
�
1�
8P�
×�
—�
—�
16�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�
2�
8P�
8PS�
—�
—�
16�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�
3�
8P�
×�
×�
—�
24�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�
4�
8PS�
×�
×�
×�
32�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�
5�
8PS�
8PS�
×�
×�
32�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�
6�
×�
×�
×�
×�
32�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�
—	: Uninstallable


×	: F8S/4S/8C/4F


A-R	: Channel No.





�
4.5.2.1 Connection of Parallel Channel Interface Cables


a.	Connect the Parallel Channel Interface cables.


� EMBED Word.Picture.6  ���


Location�
Interface Connector Panel�
Interface Connector Panel�
�
Basic�
Add.1�
(Front View of DKC)�
(Rear View of DKC)�
�
��������8P�
-


�



























�
�
�
��������������8P�
8PS�



























�
�
�
�������������8PS�
8PS�
























�
�
�
Note	T OUT : TAG OUT	B OUT : BUS OUT�T IN : TAG IN	B IN  : BUS IN


�
4.5.2.2 Connection of Serial Channel Interface Cables


a.	Connect the Serial Channel Interface cables.





� EMBED Word.Picture.6  ���








� EMBED Word.Picture.6  ���





�
4.5.2.3 Connection of SCSI Channel Interface Cables


a.	Connection the SCSI Channel Interface cables.





�
Basic�
Add. 1�
Add. 2�
Add. 3�
�






CL1�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�






CL2�
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
� EMBED Word.Picture.6  ����
�



The location of the SCSI channel interface panels are shown in the Table 4.5.2-1. Refer to DKCREP04-600.





�
4.5.2.4 Connection of Fibre Channel Interface Cables


a.	Connect the Fibre Channel Interface cables.





� EMBED Word.Picture.6  ���


� EMBED Word.Picture.6  ���





�
4.5.3 PCI Cabling


a.	Connect the PCI cables





� EMBED Word.Picture.6  ���








4.5.4 RCU Cabling


a.	Connect the RCU cables.





� EMBED Word.Picture.6  ���





Connector No.�
Enable/Disable Route�
�
JR1�
CL1  CH A, B�
�
JR2�
CL1  CH C, D�
�
JR3�
CL1  CH E, F�
�
JR4�
CL1  CH G, H�
�
JR5�
CL2  CH A, B�
�
JR6�
CL2  CH C, D�
�
JR7�
CL2  CH E, F�
�
JR8�
CL2  CH G, H�
�



	K6601527-





REV.0�
Jun.1998�
�
�
�
�
�
�
Copyright ©1998, Hitachi, Ltd.


DKCREP04-�page �63�0











CL2





CL1





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH D





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH C





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH A





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH B





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH D





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH C





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH A





B


U


S


I


N





T


A


G 


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH B





CL2





CL2





CL1





CL1





B OUT





B OUT





T OUT





CH E





CH F





T OUT





 B IN





 B IN





 T IN





 T IN





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH D





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH C





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH A





B


U


S


I


N





T


A


G I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH B





B OUT





B OUT





T OUT





CH G





CH H





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH E





CH F





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH G





CH H





T OUT





 B IN





 B IN





 T IN





 T IN





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH D





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH C





B


U


S


I


N





T


A


G


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH A





B


U


S


I


N





T


A


G 


I


N





T


A


G


O


U


T





B


U


S


O


U


T





CH B





CL1





CL2





B OUT





B OUT





T OUT





CH A





CH B





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH A





CH B





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH G





CH H





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH G





CH H





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH C





CH D





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH C





CH D





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH E





CH F





T OUT





 B IN





 B IN





 T IN





 T IN





B OUT





B OUT





T OUT





CH E





CH F





T OUT





 B IN





 B IN





 T IN





 T IN











