3.5 Installation of Hz Conversion Kit





3.5.1 Installation of Hz Conversion Kit for Disk Unit (DKU-F305I-56, DKU-F305I-65)





DKU-F305I-56	DKU305IE-14 (50Hz) to DKU305IU-14 (60Hz)


DKU-F305I-65	DKU305IU-14 (60Hz) to DKU305IE-14 (50Hz)





�EMBED MSDraw  \* MERGEFORMAT���


	Perform The Hz Conversion with care.


	This Hz Conversion is concerned with Primary Circuit.


	Perform this procedure before connecting the Power Cable Assy.


	(Turn off the circuit breakers on the power distribution panel)


	Turn off the main circuit breaker CB101 located in the AC Box.





�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1-1  Location of the Disk Unit Circuit Breakers








Table 3.5.1-1  Disk Unit Circuit Breakers


No.�
Location No.�
Breaker No.�
Remarks�
�
1�
AC BOX-**0�
CB101�
�
�
2�
AC BOX-**1�
CB101�
�
�



�
3.5.1.1 Flowchart





Remove Terminal Block Cover


(


Disconnect Power Cable Assy


(


Install Power Cable Assy


(


Attach Terminal Block Cover


(


Reset Jumper Cable (P104) Setting


(


Name Plate Changing





�
3.5.1.2 Parts List





DKU-F305I-56	DKU305IE-14(50Hz) to DKU305IU-14(60Hz)





No.�
Name of Part�
Part number�
Quantity/Unit�
Remarks�
�
1�
Power Cable Assy (IU type)�
3239396-A�
1�
�
�
2�
Nameplate (IU)�
2099649-12�
1�
�
�
3�
Label (V. Hz)�
3213180-1�
1�
�
�
4�
Label (CSA)�
5409086-1�
1�
�
�
5�
Label Noise (FCC/CSA)�
3183097-1�
1�
�
�
6�
Label (UL/CUL)�
3243606-3�
1�
�
�






DKU-F305I-65	DKU305IU-14(60Hz) to DKU305IE-14(50Hz)





No.�
Name of Part�
Part number�
Quantity/Unit�
Remarks�
�
1�
Power Cable Assy (IE type)�
3239396-B�
1�
�
�
2�
Nameplate (IE)�
2099649-13�
1�
�
�
3�
Label (V. Hz)�
3213180-1�
1�
�
�
4�
Label (CSA)�
5409086-1�
1�
�
�
5�
Label (IN)�
3228038-1�
1�
�
�
6�
Label (UL3)�
5466323-1�
1�
�
�
7�
Label (CE Mark)�
3240543-1�
1�
�
�



�
3.5.1.3 Changing Input Power Cables


Remove the fall proof adapter (only for rear side).





�EMBED MSDraw  \* MERGEFORMAT���





Fig. 3.5.1.3-1  Removal of Fall Proof Adapter





Remove the plate of the back side of the Disk Unit as illustrated in fig. 3.5.1.3-2.


		a.  Remove the two screws.	b.  Slide the plate toward the rear side to remove.


�EMBED MSDraw  \* MERGEFORMAT���    �EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-2  Removal of Plate





�
Remove the terminal block cover and disconnect the power cable Assy.


�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-3  Removal of Power Cable Assy (DKU-F305I-65)











Remove the frame ground cable for each input power cable from the frame.


�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-4  Removal of Frame Ground Cable (DKU-F305I-65)





�
Loosen the screws and remove the Power Cable Assy.


�EMBED MSDraw  \* MERGEFORMAT����EMBED MSDraw  \* MERGEFORMAT���





Fig. 3.5.1.3-5  Removal of Power Cable Assy (DKU-F305I-65)











Attach the Power Cable Assy and secure two screws.





�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-6  Installation of Power Cable Assy (DKU-F305I-65)





�
Attach frame ground cable with the screw and lock washer.


�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-7  Attachment of Frame Ground Cable (DKU-F305I-65)














�
Connect the input power cables to the terminal block and attach terminal block cover.


�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-8  Connection of Power Cable Assy (DKU-F305I-65)








Table 3.5.1.3-2 Input Power Cable Conductors Numbers


No.�
Model Number�
Input Voltage�
Input Power Cable Conductors�
Remarks�
�
1�
DKU-F305I-56�
200-240Vac�
4 conductors 


(L1, L2, L3, FG)�
�
�
2�
DKU-F305I-65�
380-415Vac�
5 conductors 


(L1, L2, L3, N. FG)�
�
�



�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-9  Connection of Input Power Cables to the Terminal Block





�
Install the jumper cable (P104) as indicated in the table below.





Table 3.5.1.3-3  Jumper Cable (P104) Locations


No.�
Model Number�
Input Voltage�
Jumper Cable (P104) Location�
Remarks�
�
1�
DKU-F305I-56�
200-240Vac�
J104-1�
(J104-2: Dummy Connector)�
�
2�
DKU-F305I-65�
380-415Vac�
J104-2�
(J104-1: Dummy Connector)�
�



�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-10  Jumper Cable P104 Setting








Re-Install the plate.





�EMBED MSDraw  \* MERGEFORMAT����EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-11  Attachment of Plate





�
Secure the plate with screws.





�EMBED MSDraw  \* MERGEFORMAT���


Fig. 3.5.1.3-12  Attachment of Plate





�
Change the Nameplate.�Refer to Fig. 3.5.1.3-13 and Fig. 3.5.1.3-14 “Location of Nameplate and Labels”.





DKU-F305I-56





a.	Change the Nameplate , Label (V. Hz) and Label (CSA).�Engrave the manufacturing number and so forth on the new nameplate and labels.


b.	Remove the Label (IN), Label (CE Mark) and Label (UL3).


c.	Put the Label (UL/CUL) and Label Noise (FCC/CSA).








DKU-F305I-65





a.	Change the Nameplate , Label (V. Hz) and Label (CSA).�Engrave the manufacturing number and so forth on the new nameplate and labels.


b.	Remove the Label (UL/CUL) and Label Noise (FCC/CSA).


c.	Put the Label (IN), Label (CE Mark) and Label (UL3).





�EMBED MSDraw���


Fig. 3.5.1.3-13  Location of Nameplate and Labels





�



�EMBED MSDraw  \* MERGEFORMAT���





Fig. 3.5.1.3-14  Location of Nameplate and Labels








Return to General Flow.�New Installation�	Basic Disk Unit Installation : Go to INST02-10 step (2)-4.�	Additional Disk Units : Go to INST02-11 step (7)-2.�Non-Disruptive Installation : Go to INST02-21 step(7)-2.�Disruptive Installation : Go to INST02-42 step(11)-2.














	K6601527-





REV.0�
Nov.1997�
�
�
�
�
�
�
Copyright ©1997, Hitachi, Ltd.


INST03-�page �64�0





REV.1�
Nov.1997�
Aug.1999�
�
�
�
�
�
Copyright ©1997,1999, Hitachi, Ltd.


INST03-�page �70�0





REV.1�
Nov.1997�
Aug.1999�
�
�
�
�
�
Copyright ©1997,1999, Hitachi, Ltd.


INST03-�page �71�0





REV.0�
Nov.1997�
�
�
�
�
�
�
Copyright ©1997, Hitachi, Ltd.


INST03-�page �74�0














