[HARDWARE T18]









Location�Function Name of Component�Part Name��Front or Rear 

upside of DKU�1�DKUMN�SZ601-A��







� EMBED Word.Picture.6  ���





Notice: Be sure to wear your wrist strap and attach to ground prior to performing the following work.  This will ensure that the IC and LSI on the PCB are protected from static electricity.



�1. The following figure(Fig. T18-1) and table(Table T18-1) show the correct way to replace the DKUMN PCB.

a. Set Enable/Disable Switch to Disable on the DKUMN PCB.

�







b. Disconnect all cables.

c. Remove the failed DKUMN PCB off the four latches.

d. Attach the spare PCB on the latches.

e. Connect all the cables.



� EMBED Word.Picture.6  ���

							Fig. T18-1  Replacement of DKUMN PCB



Table T18-1 Connection of DKUMN PCB Cables

No.�Connector No.�DKUMN-R1F�DKUMN-R1R�DKUMN-R2F�DKUMN-R2R�DKUMN-L1F�DKUMN-L1R�DKUMN-L2F�DKUMN-L2R��1�J1�P1-1�P1-2�P1-1�P1-2�P1-1�P1-2�P1-1�P1-2��2�J2�P2-1R�P2-2R�-�-�P2-1L�P2-2L�-�-��3�J3�P3-1�P3-2�-�-�P3-1�P3-2�-�-��4�J4�P4-1R�P4-2R�P4-1R�P4-2R�P4-1L�P4-2L�P4-1L�P4-2L��5�J5-A�P5A-1�P5A-2�P5A-1�P5A-2�P5A-1�P5A-2�P5A-1�P5A-2��6�J5-B�P5B-1�P5B-2�P5B-1�P5B-2�P5B-1�P5B-2�P5B-1�P5B-2��7�J6-A�P6A-1�P6A-2�P6A-1�P6A-2�P6A-1�P6A-2�P6A-1�P6A-2��8�J6-B�P6B-1�P6B-2�P6B-1�P6B-2�P6B-1�P6B-2�P6B-1�P6B-2��9�J7-A�P7A-1�P7A-2�P7A-1�P7A-2�P7A-1�P7A-2�P7A-1�P7A-2��10�J7-B�P7B-1�P7B-2�P7B-1�P7B-2�P7B-1�P7B-2�P7B-1�P7B-2��11�J8-A�P8A-1�P8A-2�P8A-1�P8A-2�P8A-1�P8A-2�P8A-1�P8A-2��12�J8-B�P8B-1�P8B-2�P8B-1�P8B-2�P8B-1�P8B-2�P8B-1�P8B-2���2. Set the switches and jumpers



a. Set the switches and install the jumpers on the DKUMN PCBs as indicated in the table below(tables T18-2 and T18-3).

b. Set Enable/Disable Switch to Enable on the DKUMN PCB.



Table T18-2  DKUMN PCB Jumper Plug Positions

No.�Location No.�S1�JP1(#1,#2,#3)�JP1(#4,#5,#6)�JP1(#7,#8,#9)�JP2�Remarks��1�DKUMN-R1F�DISABLE�#1-#2 SHORT�#4-#5 SHORT�#7-#8 SHORT�Not Used�First��2�DKUMN-R1R�DISABLE�#2-#3 SHORT�#4-#5 SHORT�#7-#8 SHORT�Not Used�Disk Unit��3�DKUMN-R2F�DISABLE�#1-#2 SHORT�#5-#6 SHORT�#7-#8 SHORT�Not Used�Second��4�DKUMN-R2R�DISABLE�#2-#3 SHORT�#5-#6 SHORT�#7-#8 SHORT�Not Used�Disk Unit��5�DKUMN-L1F�DISABLE�#1-#2 SHORT�#4-#5 SHORT�#8-#9 SHORT�Not Used�Third��6�DKUMN-L1R�DISABLE�#2-#3 SHORT�#4-#5 SHORT�#8-#9 SHORT�Not Used�Disk Unit��7�DKUMN-L2F�DISABLE�#1-#2 SHORT�#5-#6 SHORT�#8-#9 SHORT�Not Used�Fourth��8�DKUMN-L2R�DISABLE�#2-#3 SHORT�#5-#6 SHORT�#8-#9 SHORT�Not Used�Disk Unit��

No.�Location No.�Additional HDU Box Installed�No Additional HDU Box Installed�Remarks����JP3(#1,#2,#3)�JP3(#4,#5,#6)�JP3(#1,#2,#3)�JP3(#4,#5,#6)���1�DKUMN-R1F�#1-#2 SHORT�#4-#5 SHORT�#1-#2 SHORT�#5-#6 SHORT�First��2�DKUMN-R1R�#1-#2 SHORT�#4-#5 SHORT�#2-#3 SHORT�#4-#5 SHORT�Disk Unit��3�DKUMN-R2F�#1-#2 SHORT�#4-#5 SHORT�#1-#2 SHORT�#5-#6 SHORT�Second��4�DKUMN-R2R�#1-#2 SHORT�#4-#5 SHORT�#2-#3 SHORT�#4-#5 SHORT�Disk Unit��5�DKUMN-L1F�#1-#2 SHORT�#4-#5 SHORT�#1-#2 SHORT�#5-#6 SHORT�Third��6�DKUMN-L1R�#1-#2 SHORT�#4-#5 SHORT�#2-#3 SHORT�#4-#5 SHORT�Disk Unit��7�DKUMN-L2F�#1-#2 SHORT�#4-#5 SHORT�#1-#2 SHORT�#5-#6 SHORT�Fourth��8�DKUMN-L2R�#1-#2 SHORT�#4-#5 SHORT�#2-#3 SHORT�#4-#5 SHORT�Disk Unit���Table T18-3 DKUMN PCB Jumper Plug Positions

� EMBED Word.Picture.6  ���



� EMBED Word.Picture.6  ���





3. Go to post-PROCEDURE t4 (REP04-880).





	K6601527-



REV.0�Nov.1997�������Copyright (1997, Hitachi, Ltd.

REP03-�page �175�0



REV.1�Nov.1997�Jun.1998������Copyright (1997,1998, Hitachi, Ltd.

REP03-�page �176�0



REV.0�Nov.1997�������Copyright (1997, Hitachi, Ltd.

REP03-�page �177�0





� EMBED Word.Picture.6  ���

A system down may be caused by setting the Enable/Disable switch of the DKUMN PCB other than that to be replaced to "Disable".  Be sure that it is the DKUMN PCB to be replaced.








