	[image: image1.jpg]Nokia Slemens

=




	
	[image: image2.png]6

vodafone







QUALITY REPORT
(PERFORMED-ACTIVITY VERIFICATION)

BTS & MW Installation, Commissioning & Integration

  Site ID and Site Name:


	Equipment Type
	Configuration
	Check

	
	
	

	
	
	


	Subcontractor: ________________________________

	Activity
	Subcontractor Responsible

	Base Station Implementation
	

	Antenna System Installation
	

	Alarm-Panel/DDF Inst. & PCM
	

	Transmission equipment Installation
	

	Rectifier system and battery Installation
	

	Site Folder
	


	Open:
 (
Activity Completed, But Corrective Actions Required.

Activity Completed, but minor Corrective Actions are required (severity 3 or 4). 

 (
Functional Defects Found, Site Not Acceptable.

Activity Completed, but Functional Defects (severity 1 or 2) have been found. Site is not Acceptable. 

Opened by:
Name: _________________________  Signature: _______________________  Date: ____ /____ /________


	Closed:
 (
Activity Completed and Acceptable.

Activity completed and no (additional) corrective actions are required.  

Closed by:
Name: _________________________  Signature: _______________________  Date: ____ /____ /________


PUNCH LIST

This table lists ALL DEFECTS found on site, either before or during the final quality inspection. The SITE PUNCH LIST is represented by the list of those defects reported as ‘NOT OK! To Be Cleaned-up’ and which are still to be cleaned-up at the time of Inspection

	Item 

No.

[…]
	Severity

Level
(1...4)
	Cleaned Up

By
	Defect Description



	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	

	
	
	( NS (Nokia Subc.)   ( N (Nokia)
	

	
	
	( CS (Cust. Subc.)   ( C (Customer)
	


Subcontractor Representative (where present during inspection):
NAME:__________________________________SIGNED:_________________________DATE:_____/_____/_____

CHECKLIST

	Item
number
	Descri
	Severity
Level
	Check

	5001-6000
	TI IMPLEMENTATION GENERAL
	 
	 

	5401-5500
	LOGISTICS / DELIVERY
	 
	 

	5401
	Delivery as per BOQ (Hardware & instalation materials) verify physical material against BOQ.
	4
	 

	5403
	Delivery packaging without visible damages, Check Equipment for damages.
	4
	 

	6001-6500
	IMPLEMENTATION BTS
	 
	 

	6001-6100
	INSTALLATION
	 
	 

	6001
	Cabinet installed according to specifications, leveled & grouting done using insulation washer & tube and OK.
	2
	 

	6002
	Top Cover,Door and locks are properly installed & working OK.
	3
	 

	6003
	Cable entry kits and sealing installed correctly, Cabinet gaskets not damaged.
	3
	 

	6010
	Air filter installed correctly (and cleaned according to requirements)
	3
	 

	6011
	OVP boxes (both ends) for remote RF DC cable installed correctly (For tower mounted BTS)
	2
	 

	6012
	Internal Plug-in unit / Modules installed correctly as per configuration requirements.
	2
	 

	6013
	Dummy panels & Doors ground straps installed correctly
	4
	 

	6023
	OD Cabinet grouted  by using specified size nuts bolts & washers, usage of SS/Galvanized nuts bolts only. Cabinet is isolated from floor. Check for vertical & horizontal level using sprit level.
	3
	 

	6024
	BTS Cabinet grounded with specified cables and terminated to site main grounding bus bar.
	2
	 

	6026
	Door Fan sensor installed and working OK (for Ultra OD sites only)
	2
	 

	6201-6300
	COMMISSIONING
	 
	 

	6201
	DAC value measured with ferquency counter & Master clock set correctly
	2
	 

	6204
	Batteries check and measurements OK, All alarms tested, working correctly and cleared
	2
	 

	6207
	TRX Power measurements done on individual TRX's and result available in site folder
	1
	 

	6210
	Software at current Customer Equipment Release Note (ERN) version OK
	3
	 

	6221
	Freq/DAC and BTS top power measurements are checked & recorded in site folder
	2
	 

	6270
	All Plug-in-units working - visual check
	2
	 

	6301-6400
	INTEGRATION
	 
	 

	6301
	Test calls in all sectors/timeslots successful
	2
	 

	6302
	Alarm transmission towards OMC successful
	2
	 

	6303
	HWDB download from OMC to BSC correct
	2
	 

	6304
	Correct Radio Network parameters incl. Transmission data available
	1
	 

	6305
	Transmission link working properly
	1
	 

	6306
	BTS Auto recovery after power breakdown working properly
	1
	 

	6307
	Management connection verified from OMC/NOC and working correctly
	1
	 

	6308
	Softer handovers completed by walk around, where practicable, or cell lock down
	3
	 

	6501-6600
	IMPLEMENTATION ALARM PANEL / DDF SYSTEM
	 
	 

	6501-6550
	INSTALLATION
	 
	 

	6502
	Distribution panel installed correctly, Labelling done according to specifications
	2
	 

	6504
	Alarm panel installed correctly (FSEB)
	2
	 

	6505
	DDF rack  DDF module installed correctly
	1
	 

	6507
	DDF is grounded to the grounding busbar
	2
	 

	6601-6700
	IMPLEMENTATION POWER SYSTEM
	 
	 

	6601-6650
	INSTALLATION
	 
	 

	6601
	Rectifier installed according to specification and configuration
	2
	 

	6602
	Number of rectifier according to configuration and capacity of each rectifier modules
	3
	 

	6603
	Number of batteries according to configuration and capacity of each battery strings
	3
	 

	6604
	Cabinet installed according to specifications, Cover doors and locks properly adjusted
	2
	 

	6613
	Busbar installed correctly & Labelling done correctly
	1
	 

	6617
	Battery voltages has been checked and recorded prior to installation, report in site folder.
	4
	 

	6618
	Battery & Battery racks installed correctly, check for vertical and horizontal leveling.
	3
	 

	6619
	All vent plugs properly closed and tigtened properly.
	3
	 

	6621
	Petrolium jelly applied on Battery terminations, Temperature sensor installed & working correctly
	3
	 

	6627
	Cable entry kits / bridging kits and sealing installed correctly
	3
	 

	6630
	MCB/Fuse rating used for rectifier(SMPS) at PIU/ACDB
	3
	 

	6631
	MCB's /Fuses installed inside rectifier (SMPS) for Battery path & Load Path as per Specifications
	3
	 

	6671-6690
	COMMISSIONING
	 
	 

	6671
	Input voltage as per specific range. Line to nutral, nutral to earth & line to earth voltage to be checked & recorded in site folder.
	2
	 

	6672
	All alarms checked and cleared
	2
	 

	6673
	Output voltage within specific range and difference recorded in site folder.
	2
	 

	6674
	All Power System commissioning parameters entered in power system correctly.
	2
	 

	6675
	Battery Cell Voltages checked & recorded in site folder Discharge test to be conducted (should be  Isolated from Rectifier (SMPS) before checking) Minimum 1 hrs.
	2
	 

	6676
	All Modules are working properly and load are shared
	2
	 

	6670
	Charging current setting in rectifier (SMPS)  as per the specification. (Based on battery manufacturer spec) 
	3
	 

	6701-7000
	IMPLEMENTATION ANTENNA SYSTEM
	 
	 

	6701-6750
	INSTALLATION
	 
	 

	6701
	Correct antenna types on each sector as per planning documents.
	2
	 

	6703
	Tilting (mechanical &/or electrical) done according to specifications
	3
	 

	6704
	Antennas orientation according to specification
	2
	 

	6705
	Antennas properly mounted and secured
	2
	 

	6801-6850
	COMMISSIONING
	 
	 

	6801
	Measured Commissioning results & parameters are within specified range (VSWR, Power,Insertion loss)
	2
	 

	6802
	Measures executed with calibrated instruments (Power meter & site master)
	2
	 

	7001-7800
	IMPLEMENTATION TRANSMISSION SYSTEM
	 
	 

	7001-7100
	TRANSMISSION RACKs INSTALLATION
	 
	 

	7001
	Rack(s) installed at specified position as per site layout.
	3
	 

	7002
	Rack(s) grouted correctly & Rack(s) grounded correctly, to check horizontal & vertical.
	3
	 

	7201-7300
	INDOOR UNIT INSTALLATION
	 
	 

	7201
	Indoor Unit installed at specified position as per site plan.
	3
	 

	7202
	Indoor Unit grounded correctly
	2
	 

	7203
	Indoor Unit power connection correct
	2
	 

	7204
	Indoor Unit labelled correctly
	4
	 

	7301-7400
	OUTDOOR UNIT INSTALLATION (including dish)
	 
	 

	7301
	Installation done like shown in the site planning documentation (pole, direction, height,…) 
	3
	 

	7302
	Alignment unit and antenna are installed properly and screws are tightened,Side Strut installed properly for Antenna dia >=1.2
	2
	 

	7303
	Antenna polarisation according to specifications, The serial number of the antenna is recorded in site folder
	1
	 

	7304
	Coupler & Waveguide is properly mounted (Separate antenna or HSB configuration)
	2
	 

	7306
	OU is installed properly (screws are tightened, sealing is in right position)
	2
	 

	7307
	Enough space left for removing Outdoor Unit, OU is grounded properly & Labelled Properly
	4
	 

	7501-7600
	CABLING 
	 
	 

	6551
	RF & IF Cables preparations (stripping  cutting) & installation according to specifications
	2
	 

	6552
	RF & IF Cables labelled correctly
	3
	 

	6553
	Cross-connections positions of E1's at DDF according to specifications and labelled correctly
	3
	 

	6555
	RF & IF Cable installed over specified route & routed using cable supporting clamps & without sharp bends.
	4
	 

	6560
	Feeder & Flex Bus cable  Grounding done correctly according to specifications
	2
	 

	6653
	AC & DC cable routing done as per specificatiions.(PVC conduits to be used for OD BTS sites if installed outside shelter)
	3
	 

	6655
	All feeder & IF connector tightened to specified torque.
	2
	 

	6751
	Jumper installed correctly without sharp bends. 
	3
	 

	6752
	Feeder & IF cable entry thru WFT be installed with drain loop and sealed against water ingression.
	3
	 

	6755
	EMPs / surge suppressor properly installed and grounded
	2
	 

	6757
	Waterproof on connectors according to specifications
	3
	 

	6758
	Grounding kits number and positioning according to specifications
	3
	 

	7503
	Q1 bus cable properly installed.
	3
	 

	7508
	OU connector is sealed according to specifications  
	2
	 

	7509
	External PCM & Alarm Cable routed through PVC Conduit(For OD BTS installed outside shelter)
	2
	 

	7510
	External Fiber Optic cables installed correctly, cleaned and tested
	2
	 

	7601-7700
	COMMISSIONING / INTEGRATION
	 
	 

	7601
	Transmit frequency checked  (according to planning data)
	1
	 

	7603
	BER test with the hardware loop passed
	2
	 

	7606
	Radio alarms checked, No active alarms on the link
	3
	 

	7608
	Recieve level correct (within +/- 4 dB from calculated receive signal)
	2
	 

	7609
	All tests passed and radio levels within specified limits
	2
	 

	7610
	Identification data correct of microwave link.
	4
	 

	7612
	Link Q1 address set and integrated
	2
	 

	7613
	Interleave setting (default OFF), ALCQ setting (default OFF)
	2
	 

	7615
	Operating mode and station type set correctly
	2
	 

	7616
	Fade margin test results within specified limits
	2
	 

	7617
	Customer Specific Commissioning & Parameters correct
	2
	 

	7618
	All microwave commissioning data and results correct
	3
	 

	7650
	Others
	 
	 

	7651
	Others
	 
	 

	7652
	Others
	 
	 

	7653
	Others
	 
	 

	7654
	Others
	 
	 

	 
	FINAL CHECK/ACCEPTANCE
	 
	 

	 
	Left over/ excess material reconsilled and accounted for, list in site folder. 
	3
	 

	 
	Site is cleaned properly and housekeeping done.
	3
	 

	 
	Material Delivery Vs utilised measured and recorded in site folder.
	3
	 

	 
	Site handover details completed in site folder.
	 
	 

	 
	TI Acceptance Certificate done with subcontractor/ authorities/customer according to specifications.
	3
	 

	 
	Self Assessement quality audit done by sub con, loaded in E-pm, 100% punch points cleared, check list copy is available on site in site folder.
	3
	 


	© Nokia Networks
	BTS & MW Installation, Commissioning & Integration
	 Page  2



[image: image1.jpg][image: image2.png]_1272901379

