## Slide 1: EHS Introduction

## Slide 2
The document describes the various safety accidents caused by misoperation and lack of relevant safety knowledge in practice and introduces corresponding ways to avoid them, with a view to ensuring a safe environment.

## Slide 3
Upon completion of this course, you will be able to:
  Understand the importance of safety training;
  Understand causes of accidents in work;
  Understand ways to avoid accidents;
  Understand how to implement protection.

## Slide 4
Introduction to EHS
Accident Probability and Personnel Qualification
PPE Protection Overview
Engineering Construction Safety

## Slide 5: Introduction to EHS (1)
Concept
  EHS is short for environment, health, and safety.
  The EHS management system establishes a systematic prevention and management mechanism to minimize various accidents, environmental hazards, and occupational diseases. It improves the safety, environment, and health performance of enterprises.
Environment
Health
Safety

## Slide 6: Introduction to EHS (2)
Functions
  Helps enterprises meet the laws and regulations on environment, health, and safety.
  Helps protect the environment and meet the requirements of the strategy for sustainable development.
  Helps maintain the reputation of enterprises and enhance their competitiveness.
  Helps reduce enterprise costs and save energy and resources.
  Helps reduce the occurrence of various accidents and ensure the health
  and safety of employees.
  Helps meet public expectations and maintain favorable public and
  social relationships.
  Helps enterprises effectively combine economic benefits, social
  benefits, and environmental benefits.
Environment
Health
Safety

## Slide 7
Introduction to EHS
Accident Probability and Personnel Qualification
PPE Protection Overview
Engineering Construction Safety

## Slide 8: Heinrich's Law
A famous U.S. safety engineer Heinrich induced Heinrich's Law in 1931. He counted 550,000 mechanical accidents, including non-injury accidents, 1666 fatalities and serious injuries, and 48,334 minor injuries. Later, he came to an important conclusion: the proportion of casualties (serious injuries and deaths), minor injuries, and unsafe behaviors in mechanical accidents was 1:29:300. This law of accidents is internationally recognized.
No accident does not mean no accident will occur.
Casualties
Minor injuries
Unsafe behaviors
1
29
300
Notes: For different production processes and different types of accidents, the preceding proportion relationship may not be the same. However, this statistical rule indicates that in the same activity, numerous accidents inevitably lead to major casualty accidents. To prevent the occurrence of major accidents, we must reduce and eliminate non-injury accidents, and pay attention to the risks of accidents and near misses. Otherwise, serious accidents will occur.
Tip of the iceberg

## Slide 9: Staff's Mental Status Affects the Probability of Accidents
Four states
  Rush
  Complacent
  Fatigued
  Frustrated
Four possible results
  Eyes away
  Absent-minded
  Dangerous areas
  Imbalanced/dragged/clipped
These errors increase the injury risk

## Slide 10: Sufficient Preparations to Reduce Fatal Errors
Electricians must have good health and be free of diseases or physiological defects that affect their work, such as mental disease, heart attack, faint, and color blindness.
Operators must be well rested before performing an important operation. Working under fatigue is not allowed.
Huawei equipment can be installed, operated, and maintained only by personnel who have received a thorough training, understand all necessary safety precautions, and are able to correctly perform all operations.
Only trained and qualified personnel are allowed to install, operate, and maintain the equipment.
Only personnel certified or authorized by Huawei are allowed to replace or change the equipment or components (including software).
When operating the equipment, comply with local laws and regulations. The safety instructions in the document are only supplements to the local laws and regulations.

## Slide 11
Introduction to EHS
Accident Probability and Personnel Qualification
PPE Protection Overview
Engineering Construction Safety

## Slide 12: PPE Protection (1)
Definition
  The production process is filled with dangerous and harmful factors, which harm workers' bodies and health and even endanger their lives. Personal protective equipment (PPE) refers to articles workers wear during production to avoid or reduce accidents and occupational hazards.
Functions
  Protects our bodies against harms incurred by equipment or facilities during production, namely, to prevent work-related injuries.
  Effectively ensures our health and prevents us from occupational diseases.
  Though all production processes are filled with dangerous and harmful factors, correctly using and wearing PPE is an effective measure to ensure work safety.

## Slide 13: PPE Protection (2)
No. | Operation |  | Mandatory PPE | Recommended PPE
1 | Operations involving objects falling and colliding |  | 1. Safety helmet; 2. Protective shoes | Safety net
2 | Operations with flying scraps |  | Shock-proof goggles | 
3 | Operations involving sharp instruments |  | Anti-mechanical harm gloves (cut resistant gloves) | 
4 | Low-voltage (below 1 kV) electric operations |  | 1. Insulation gloves; 2. Insulation shoes | Insulation protective clothing
5 | High-voltage electric operations | 1–10 kV | 1. Insulation gloves; 2. Insulation shoes; 3. Insulation protective clothing | 
6 |  | 10–500 kV | Electricity shielding clothing | 
7 | Operations involving high temperature substances |  | High-temperature resistant gloves | 
8 | Operations involving low temperature substances |  | Low-temperature resistant gloves | Low-temperature resistant clothing
9 | Operations at heights |  | 1. Safety helmet; 2. Safety belt | Safety net
11 | Operations involving toxic substances |  | 1. Chemical resistant gloves; 2. Gas mask | 
12 | Operations with corrosive substances |  | 1. Anti-corrosion goggles; 2. Acid and alkali resistant gloves; 3. Acid (alkali) resistant clothing | Chemical resistant shoes
13 | Operations with pollution risks |  | 1. Acid and alkali resistant gloves; 2. Chemical resistant clothing | 

## Slide 14: PPE - Head Protection
Head Protection
  Safety helmet: special protective equipment
    Three certificates: production license, product qualification certificate, safety sign/safety authentication certificate).
  Common head protection equipment : safety helmet and ESD cap.
ESD cap
Safety helmet

## Slide 15: PPE - Facial Protection
Facial Protection
  Facial protection refers to wearing protective articles to protect your eyes and face from smoke, dust, metal sparks, flying scraps, heat, electromagnetic radiation, laser, and chemical splashes.
  Common facial protection equipment: laser safety glasses, goggles, and protective masks.
Protective masks
Welding mask

## Slide 16: PPE - Hand Protection
Hand Protection
  Gloves worn by workers during production to protect their hands and arms are called “hand protection equipment”.
  Common hand protection equipment: rubber protective gloves (to prevent corrosion against acid, alkali, and other dangerous and chemical substances), finger cots, heat- and cold-resistant gloves, cut resistant gloves, and cotton gloves.
Finger cots
Cut resistant gloves
Cold-resistant gloves
Rubber protective gloves

## Slide 17: PPE - Foot Protection
Foot Protection
  Protective wears used to protect the workers' feet against hazardous substances and energy.
  Common foot protection equipment: ESD shoes, puncture-proof shoes, high-temperature resistant shoes, insulation protective shoes, and acid and alkali resistant shoes.
ESD shoes
Insulation protective shoes
Puncture-proof shoes

## Slide 18: PPE - Falling Protection
Falling Protection
  Working at heights refers to operating at a height of 2 m or more with the possibility of falling down, such as installing high towers or cleaning walls of high buildings.
  Securing workers operating at heights to a fixed object using a rope or belt to avoid falling from heights or making a net under the working region to protect those workers who accidentally fall from the heights.

## Slide 19
Introduction to EHS
Accident Probability and Personnel Qualification
PPE Protection Overview
Engineering Construction Safety

## Slide 20: General Safety
Personal safety
  Do not operate the equipment or cables during thunderstorms.
  Wear electrostatic discharge (ESD) clothing, ESD gloves, and an ESD wrist strap before operating equipment such as an uninterruptible power system (UPS) and air conditioner. Remove conductive objects such as jewelry and watches to avoid electric shocks or burns.
  In the outbreak of fire, evacuate the building or equipment area and press the fire alarm bell or make a fire call. Do not enter the burning building again in any case.
  Grounding requirements (for the equipment that need to be grounded)
  Ground the equipment before installing it. When removing the equipment, remove the ground cable at last.
  Do not damage the ground conductor.
  Do not operate the equipment when the ground conductor is not installed. Before operating the equipment, check its electrical connection to ensure it is reliably grounded.
  Regulatory requirements
  Comply with local laws and regulations when operating the equipment. The safety considerations in the product manual are only supplements to the local safety regulations.
  Only qualified and trained personnel are allowed to install, operate, and maintain the equipment.

## Slide 21: Handling (Loading) Safety (1)
Manual handling safety
  A quarter of accidents are related to handling.
  Handling accidents account for 6% of serious accidents.
  Most handling accidents cause a loss of more than three workdays.
  Most handling accidents cause back muscle strains or sprains.
  Muscle sprains or strains are mostly caused by improper force and (or) prolonged force. Incorrect posture and excessive repetitive movements are the main causes of muscle sprains or strains.
  Muscle strains and sprains are hard to fully recover.
Chart: Injury types in handling accidents
| Sprain | Fracture | Scratch | Contusion | Epidermis injury | Other
Injury types in handling accidents | 0.65 | 0.05 | 0.07 | 0.07 | 0.09 | 0.07

## Slide 22: Handling Safety (2)
Preventive measures (1)
  Improve the layout and logistics and storage location of loads.
  Improve the carrying efficiency.
  Try to keep the load you push in the direction consistent with that your eyes see and pull the load instead of carrying it.
  Control the carrying frequency to reduce fatigue.
  Have flexible rest time.
  Ensure adequate space when carrying loads in partnership. Hold the load firm and carry it in a coordinated manner.
  Wear PPE accessories that do not bring safety risks.
  The auxiliary transporting equipment should be in good condition.

## Slide 23: Handling Safety (3)
Preventive measures (2)
  Reduce workload.
  Reduce load volume.
  Facilitate the control of load.
  Keep the surface of the package clean and free from dirt, oil stains, and corrosive products.
  Ensure that the package is free from sharp edges, unfilled corners, and rough surface.
  Avoid scalding or frostbite by using auxiliary equipment and PPE.

## Slide 24: Handling Safety (4)
Preventive measures (3)
  Reduce space obstacles.
  Ensure that the ground or work surface is in good condition.
  Do not carry load on a steep slope.
  When carrying objects on the ground of great height difference, use stairs or slopes as transition to facilitate the load carrying.
  Avoid strong wind interference.
  Lighting.

## Slide 25: Mechanical Safety
Drilling holes
  Remove cables inside a cabinet before drilling holes on the cabinet.
  Wear a pair of goggles when drilling holes to protect your eyes from metal scraps.
  Wear protective gloves when drilling holes.
  Prevent metal scraps from falling into the cabinet. Clean up metal scraps in time after drilling.
  Fans
  Place the component, screws and tools in a safe place when replacing a component. If any of them fall into an operating fan, the fan and relevant equipment will be damaged.
  Do not insert your fingers and boards into the operating fan until the fan is switched off and stops running when replacing a component near a fan; otherwise, you may get hurt or damage the equipment.
Fan

## Slide 26: Electrical Safety (1)
Personal safety refers to the safety of personnel in electrical operations. The following lists the two main causes.
Lack of electrical safety knowledge.
Non-compliant acts.
Equipment safety refers to the safety of electrical equipment and auxiliary devices.
Notes: Example: Got electric shock due to carelessness

## Slide 27: Electrical Safety (2)
Electric Current Effects to the Human Body
  Ventricular fibrillation: When the heart quivers instead of pumps due to disorganized electrical activity in the ventricles. It results in cardiac arrest with loss of consciousness and no pulse.
  Suffocation: When the current flows through the respiratory center in brain, it inhibits the breathing; when excessive current flows through the chest in a certain time, it leads to abnormal contraction of chest muscles, resulting in respiratory arrest.
  Electric shocks also bring intense spasm, causing secondary accidents, such as tumble and falling.

## Slide 28: Electrical Safety (3)
Current intensity: The higher the current, the greater the harms to human bodies.
Energized duration: The longer the energized duration, the lower the body impedance, and the greater the harms of electric shock.
  International Electrotechnical Commission (IEC) stipulated that the contact voltage threshold (equivalent to the safe voltage) is 50 V, and that no preventive measures against electric shocks are needed for 25 V or lower voltages.
Notes: Sensing current: minimum value of electric current sensed by human bodies. Average sensing current ranges from 0.7–1.1 mA. In general, sensing current brings no harm to human bodies.
Let-go current: maximum value of electric current through the body of a person at which that person can release himself or herself. Average let-go current ranges from 10–16 mA. In general, let-go current can be tolerated and cause no harms.
Deadly current: minimum value of electric current that endangers life within a short time. 100 mA and higher current causes death. When the current is below DC 50 mA and industrial frequency 30 mA, it does not pose life risks. (So, DC 50 mA and industrial frequency 30 mA are regarded as the upper thresholds of safe current.)

## Slide 29: Electrical Safety (4)
Protective Grounding and Protective Connecting to Neutral
  Protective grounding means that a certain point of electrical devices or energized circuits is directly connected to the ground, or a certain point of the de-energized part is manually connected to the ground.
    Working grounding refers the connection to the ground with a view to ensuring the normal operation of the power system, for instance, the neutral point grounding in the three-phase and four-wire low-voltage power distribution system.
    Safe grounding refers to the connection to the ground with a view to ensuring personal and equipment safety, including protective grounding (against electric shocks), surge protection grounding, ESD grounding, and shield grounding.
Notes: Note: Metal parts that pose dangerous voltage risks due to insulation damage or other causes must be grounded. Metal shells of electrical devices, such as motors, transformers, switches, and lighting devices, should all be grounded. In common low-voltage systems, ground resistance should be less than 4 ohms.

## Slide 30: Electrical Safety (5)
Protective Grounding and Protective Connecting to Neutral
  Protective connecting to neutral: refers to connecting the non-energized part of electrical devices in normal circumstances to the neutral wire of the power grid. It is worth noting that in the three-phase and four-wire power system, metal shells of the electrical devices are both grounded and connected to the neutral wire. This measure is called "repetitive grounding protection."
Notes: Note: Installing fuses and switches in the ground cable loop is not allowed.

## Slide 31: Electrical Safety (6)
Surge Protection Measures
  SPD types: Lightning rod, lightning wire, lightning net, lightning belt, and surge protector.
Tips for individual lightning protection
  Do not stay in open areas, mountain tops, ridges, or rooftops.
  Do not stay near iron gates, metal clotheslines, and railway tracks.
  Do not stay in the swimming pool, lakes, or seaside or under isolated trees.
  Close doors and windows to avoid flank-striking lightning or lightning balls.
Notes: In general, the lightning rod is used to protect the outdoor power transformation and distribution devices, buildings, and structures. The lightning wire is used to protect the power cables.
The lightning net and belt are used to protect the buildings. The surge protector is used to protect the devices.

## Slide 32: Electrical Safety (7)
Measures against body ESD accidents
  Use ESD floor/shoes/socks (static electricity conducted to the ground from feet).Put on ESD footgear and stand on the ESD floor, mats, and carpets to form a combined grounding.
  Wear an ESD wrist strap and ground it (static electricity conducted to the ground from hands).Discharge the static electricity on the body from hands. The ESD wrist strap is composed of an ESD elastic, snap, spring, resistor, and plug/clip. The inner layer of the elastic is braided with ESD yarns and the outer layer is braided with common yarns.

## Slide 33: Electrical Safety (8)
Establish comprehensive safety regulations and rules, and enhance the related education and trainings.
Electrical operations must be performed by qualified personnel. Personnel without related certificates must not maintain or repair electrical devices or perform unauthorized operations.
Electrical device safety
  The electrical devices should be protected from corrosion and moisture.
  The metal shells of electrical devices must be grounded (or connected to the neutral wire).
  Do not use electrical devices over their rated values.

## Slide 34: Electrical Safety (9)
Check the following items of instruments before working.
  Insulation condition.
  Validity period.
  Voltage level.
Implement the work ticket system when checking, maintaining, or cleaning the power-off electrical devices.
To check, maintain, or clean the power-off electrical devices, the following safety measures must be taken.
  Power off.
  Check the power.
  Install the ground cable.
  Hang a sign and set a shelter.

## Slide 35: Electrical Safety (10)
Precautions Against Ground Cable Installation
  All ground cables and the energized parts should be kept a proper distance required by regulations.
  After checking that the device under maintenance is non-energized, promptly ground the device and perform a three-phase short circuit.
  The ground resistance must meet requirements.
Precautions Against Power Check
  Put "Do not switch on." signs on handles that can power on the device.
  Do not move or remove the shelter, ground, or other signs without
  permission during the construction.
Operations performed after power-off must be carried out under supervision.
Disconnect the power supply before you carry or move electrical devices.

## Slide 36: Electrical Safety (11)
Notes: Tips: diagrams for socket connections

## Slide 37: Welding Safety (1)
Welder shells must be grounded or connected to the neutral wire. Only electricians are allowed to install or uninstall the welder power system. The insulation resistance between the winding and iron core as well as between the winding, lead, and shell should not be less than 0.5 mΩ in the primary and secondary winding self-check of the welder.
The welder should be put in a rainproof place with good ventilation. Do not put combustible or explosive articles at the welding site. Wear protective equipment as required before welding.
Welding tongs and cables must be well insulated and securely connected. Wear gloves before changing welding rods. When working in a damp environment, stand on the insulation rubber or wooden floors.
Do not weld pressurized containers or pipes. Power off the electrical devices before welding them.
Disconnect the power supply first before moving the welding cables as the working sites change. Do not climb a ladder holding welding cables.
Clear the welding slag using the electric arc and wear protective glasses in the process to protect yourself.

## Slide 38: Welding Safety (2)
Outdoor welding operations are not allowed in thunderstorm days.
Obtain a permit from relevant departments before welding in combustible and explosive gas and liquid diffusion areas.
After the welding, disconnect the power supply from the welder, and check the site. Ensure that there is no fire hazard at the site before leaving.
If combustible or explosive articles are stacked near the welding site, do not weld until they are completely removed or effective safety measures are taken.
If a welding machine is on fire, disconnect the power supply from it first.
Extinguish the fire using CO2 or 1211 fire extinguishers. Do not use the foam fire extinguisher.
Apply for the fire operation approval and surveillance measures in accordance with the site firefighting system before welding.

## Slide 39: Battery Safety
Basic protective measures (before battery installation and maintenance)
  Use dedicated insulated tools.
  Wear protective goggles and take other necessary protective measures.
  Wear rubber gloves and a protective coat to guard against electrolyte overflow.
  Battery short circuit
  To avoid battery short circuit, do not maintain batteries with power on.
  Hazardous gas
  Lead-acid batteries in use emit flammable gas. Take ventilation and fireproofing measures at the sites where lead-acid batteries are used.
  Electrolyte leakage
  Protect your skin and eyes from electrolyte leakage. If your body meets electrolyte leakage, wash with clean water immediately and visit a doctor.
A battery accident in an equipment room
Notes: Protect a lithium battery from mechanical vibration, collision, punctures, and strong impact. Otherwise, the battery may catch fire.
Battery short-circuits may cause personal injury. The high transient current generated by a short-circuit may release a surge of energy and cause fire.
The lithium battery is an enclosed battery system and will not release any gases under normal operations. If the lithium battery is severely misused, for example, being burned or thunderstruck, the battery may be damaged, resulting in electrolyte leakage. Because the electrolyte is of organic carbonate nature, it may produce CO2, CO, and N2 after being burned.
On April 5, 2017, a battery string accident occurred in the network equipment room of Beijing University of Posts and Telecommunications. As a result, the networks of multiple universities in Beijing were interrupted.

## Slide 40: Air Conditioner Safety (1)
High temperature and high pressure
  Misoperation may cause high system pressure, which leads to the refrigerant system to crack or explode.
  Pay attention to high-temperature components, such as the compressor, refrigerant pipe and electric heater.
  Pay attention to high-pressure components, such as the compressor and refrigerant pipe.
  Refrigerant frostbite
  Refrigerant leakage may cause frostbite. Take protective measures (such as wearing goggles and antifreeze gloves) when handling refrigerant.
  Pay attention to low-temperature components, such as the evaporator.
  High-speed operation
  Pay attention to high-speed rotational components, such as fans.
Precision air conditioner

## Slide 41: Air Conditioner Safety (2)
Temperature of the R410a refrigerant can be as low as –52°C the second it ejects from the cylinder, which can instantly frostbite human skins and underlying muscles, and the frostbitten skins become necrotic. In addition, if humans inhale too much refrigerant in a short time, they are likely to be suffocated to death. Therefore, having a general knowledge of refrigerant leak types in operating air conditioners and familiarizing with the related countermeasures are crucial in ensuring the safety of operators.
Minor leaks: If minor leaks occur in the pipe connection points or welding positions during the system running, tighten the connection ports, or re-weld the faulty positions after the system refrigerant is released. Minor leaks bring no personal injuries.

## Slide 42: Air Conditioner Safety (3)
Before welding the connection point of the indoor and outdoor units, completely exhaust nitrogen from the units, and ensure that related parts are in good condition.
Wear protective goggles and antifreeze gloves when refrigerant is involved in the operation.
A nitrogen reducing valve must be equipped when operating the nitrogen cylinder.
Goggles
Antifreeze gloves
Nitrogen reducing valve

## Slide 43: Air Conditioner Safety (4)
Pipe break or needle valve plug damage: When the air conditioning pipes break or the needle valve plug is damaged, there will be major refrigerant leaks. The following lists the correct way to solve this problem.
Promptly open the doors of the air conditioner cabinets in a safe place.
Evacuate all persons in the air conditioner room.
Open all doors and windows that can be opened.
After refrigerant in the air conditioning system leaks out completely and the air inside the air conditioner room is safe to breathe (no obvious smell), you are allowed to continue the next operation.
Note: In the event of major refrigerant leaks, do not try to stop the leak.

## Slide 44: Air Conditioner Safety (5)
Refrigerant cylinder damage: When the upper body of the refrigerant cylinder breaks or the safety port bursts, there will be major refrigerant leaks. The following lists the correct way to solve this problem.
Promptly open the doors of the air conditioner cabinets in a safe place.
Evacuate all persons in the air conditioner room.
Open all doors and windows that can be opened.
After refrigerant in the cylinder leaks out completely and the air inside the air conditioner room is safe to breathe (no obvious smell), you are allowed to continue the next operation.
Note: In the event of major refrigerant leaks, do not try to stop the leak.

## Slide 45: Air Conditioner Safety (6)
Connection pipe damage during refrigerant charging: If leaks occur due to breaks or damage of the connection pipe during the refrigerant charging, promptly close the valves on both sides, and replace the connection pipe. If there is only one valve, (for example, the pipe is connected to the needle valve), promptly close the valve, disconnect the pipe from the other end, and then replace the connection pipe.
Note: If one end of the connection pipe is disconnected due to leaks at that end, promptly place a heavy object on the pipe so that the high-pressure gas ejection will do no personal harms. Then, proceed following preceding instructions.

## Slide 46: Air Conditioner Safety (7)
Internal and external fans are high-speed rotational components, pay attention to the following instructions when maintaining them.
  When maintaining the fans, motors, or adjacent components (such as fan guards), disconnect their power supply, and lock the power supply hangtag.
  When operating such as maintaining adjacent the fans, prevent dropping tools or other articles in the rotating fans, because broken fans or other pieces flying out might hurt someone.
  Do not wear hangers, such as necklace, employee ID card, and bracelet, when operating rotational components.

## Slide 47
(Multiple)Which of the following measures can reduce risks during transportation?
  Control transportation frequency and reduce fatigue
  Proper use of personal protective equipment
  Avoid strong wind interference.
  Good lighting conditions
Notes: Answer: ABCD

## Slide 48
Introduction to EHS
Accident Probability and Personnel Qualification
PPE Protection Overview
Engineering Construction Safety

## Slide 49
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 51
HCIA-DCF
DCF
2.0
Guobian/wx337261
2017.05.17
Lishaofeng/l00486775
New
WangCong/wx760444
2020.4
Lishaofeng/l00486775
Notes: 2015.7.4
  调整版权和页码对齐，位于参考线8.5到8.9之间。
2015.7.14
  新增更多信息和推荐的样例。
2015.8.3
  胶片主体和备注页，段落设置为“允许标点溢出边界”。
2015.8.4
  删除缩略语页。
2015.9.2
  新增备注页页眉，居于备注页正上方，显示本章标题。
2015.9.14
  删除“谢谢”那页的白色“谢谢”。
2017.11.8
  调整母版中标题宽度。