## Slide 1: Data Center Facility Knowledge

## Slide 2
This slides describe the development, key components, common standards, and common energy consumption indicators of the data center infrastructure.

## Slide 3
Upon completion of this course, you will:
  Know the history of data center development;
  Know the common standards of data centers;
  Know the composition and energy consumption indicators of data centers;
  Know the Huawei data center products.

## Slide 4
Introduction to Data Center Development
Composition of Data Center Infrastructure
Introduction to Data Center Standards
Common Energy Consumption Indicators
Panorama of Huawei Data Center Solutions

## Slide 5: Development History of Global Data Centers
In 1942, the first electronic digital universal computer was born.
Before 1990, data centers were mainly used for government and scientific research applications, but seldom for commercial applications. Data centers were large yet few.
From 1991 to 2000, Internet companies emerged, so did commercial data centers. These data centers were small, but they increased gradually.
From 2001 to 2011, the data volume from governments, the Internet, and financial transactions soared. Governmental and commercial data centers began to develop rapidly.
Since 2012, cloud data centers have become a new trend around the globe thanks to the increase of data center technologies and applications.
Notes: Since 2012, Internet data centers (IDCs) have been integrated and upgraded. Large scale, professionalization, and environmental protection have become the leading features.

## Slide 6: Data Center Infrastructure Development Trend - Modular Data Center
Small and medium data centers are constructed to be simple, easy to use, reliable, and controllable in operation and maintenance (O&M). Compared with traditional data centers, modular data centers have unparalleled advantages in the four aspects.
  Integrated modular data centers are constructed quickly and have low requirements on the deployment environment.
  Modular products can be pre-integrated and pre-commissioned in the factory in advance. They also provide the intelligent management function.
For large data centers, the power density of information IT equipment is increasing. Modular data centers adopt in-row closely coupled cooling, which greatly improves the cooling efficiency. This adapts to the development trend of high power density.

## Slide 7: Data Center Infrastructure Development Trend - Cloud Data Center
The application and deepening of cloud computing promote the transformation of data center construction, operations management, and service modes.
  Data traffic explosion, shared infrastructure, and improved resource utilization drive large-scale data centers.
  Cloud computing enables flexible expansion, dynamic allocation, and centralized management and control of data centers.
  The construction of cloud data centers creates new growth points and promote industry adjustment, transformation, and upgrade.
  As the power consumption of data centers increases, a more efficient and energy-saving cooling system is required.

## Slide 8: Data Center Infrastructure Development Trend - Environmental Protection
With the rapid development in informatization, the construction of global data centers is accelerated. Their power consumption accounts for 1.1% to 1.5% of the global total.
Clean energy, such as wind and solar energy, is increasingly used in data centers.
There is a call for saving energy and reducing consumption to reduce power usage effectiveness (PUE) of data centers.
Notes: Three-year action plan (2018-2020) for promoting the construction of next-generation information infrastructure in Shanghai to improve the city's energy level and core competitiveness: The comprehensive PUE of new data centers should not exceed 1.3.
Guidelines for Further Strengthening Energy Conservation and Emission Reduction in the Communications Industry: Optimize the layout of cold and hot air in equipment rooms, and adopt measures such as precise air supply and quick cooling of heat sources.
  Modular data center
Energy conservation and consumption reduction are common. However, the future trend is to make them more comprehensive, efficient, and properly regulated.

## Slide 9: Data Center Infrastructure Development Trend - Intelligent Management
Inefficient data centers lead to high costs, and data center infrastructure management (DCIM) is of vital importance.
  Manage and monitor IT equipment, facility equipment, and IT processes in a unified manner.
  Support resource management and asset management.
  Support technologies such as real-time information, simulation, and remote monitoring.
Notes: DCIM: Data Center Infrastructure Management
Intelligent terminals, virtual reality (VR), artificial intelligence, wearable equipment, and Internet of Things (IoT) also promote intelligent management of data centers.

## Slide 10: Introduction to Data Center Lifecycle
Planning
Design
Construction
Operation & Maintenance
Evaluation
Notes: For details about the five phases, see Fundamentals of Managing the Data Center Life Cycle for Owners—Schneider Electric.
Plan: This phase is the key to the success of the entire data center project. In this phase, the data center owner and manager need to build the prototype of the system architecture and project budget, and select the model design for the system. They also need to identify and determine the factors that may affect the system design. Once the system concept is defined, it is possible to prepare the site selection assessment.
Design: The core content of the design phase is to convert the planning result into diagrams and construction documents. In this phase, it is equally important to ensure that the right people join the project at the right time. The design team should include IT and design engineers, possibly even architects and mechanical, electrical, and water supply and drainage engineers. The construction team consists of electrical, network, mechanical, low-voltage contractors and subcontractors. The data center owner or manager is responsible for selecting these teams and reviewing all design achievements.
Build: In this phase, the documents of the construction team and the professional skills of the equipment supplier are combined. The phase is an excellent opportunity for the management team and employees to learn and improve. Commissioning can bring valuable documents to help improve equipment operating status. Although commissioning is not completely necessary, it helps the entire team better understand the complexity of the data center by detecting the response of the entire system to external inputs and external changes.

## Slide 11
Notes: Operate: This is the longest and costliest phase in the data center lifecycle. It may last for up to 20 years. Successful O&M projects require effective management of environmental health and safety, personnel management, emergency preparedness and response, training, performance monitoring, maintenance, archiving, infrastructure, quality, energy, and finance.
Assess: This phase is often overlooked. However, it actually provides a lot of valuable information and feasibility advice for understanding how the operator and infrastructure system operate. Analyze the power supply, cooling, space capability, and usage trend continuously and periodically to better determine whether the infrastructure meets the design intention. The assessment phase also includes the appraisal of employee efficiency and O&M project performance. In the five phases, O&M mainly involves operation and assessment. To better understand the data center, the O&M team can participate in the planning phase. For details about the periodogram, see Data Center O&M Management Standards.

## Slide 12
Introduction to Data Center Development
Composition of Data Center Infrastructure
Introduction to Data Center Standards
Common Energy Consumption Indicators
Panorama of Huawei Data Center Solutions

## Slide 13: Composition of the Data Center Facility
Precision air supply cabinet
IT device cabinet
DG & ATS
UPS
DC power cabinet
AC power cabinet
Static transfer switch
Battery and battery rack
Power cable
Cable tray
Optical distribution frame
Cables & fibers
Route label
Cabling rack
Fire detection system
Smoke detection system
Fire extinguishing system
Floor plan
Doors & windows
Walls & ceilings
Raised floor
Lighting
Transient surge voltage suppression device
Ground protection system
Cabinet system
Interior decoration
Power supply system
Surge protection/ grounding
Firefighting system
Integrated cabling
Cooling system
Integration management
Integration management
Access control
CCTV
Power and environment monitoring
Precision air conditioner
Comfort air conditioner
Ventilation system
Notes: We have talked about the function room and classifications of the infrastructure hierarchically. Next, we will talk about its systems and compositions.
As we all know, the data center site infrastructure is an integration of many subsystems. This is a figure about the Layer 1 of Huawei data center infrastructure. From this figure, we can see that the infrastructure contains eight systems.
Power supply system: It includes the DG, ATS, UPS. DC cabinet, AC cabinet, static transfer switch, storage battery, battery rack, and power cables.
Cooling system: It includes the precision air conditioner, comfort air conditioner, and ventilation system.
The other six systems include the interior decoration, cabinet, surge protection/grounding, fire-fighting, integrated cabling, and integration management, all of which contain some components. We will skip them here.
We find that the eight systems defined here put much emphasis on products, for example, speaking of the power distribution system, we tend to emphasize the DG, ATS, and UPS under the system. Though this classification is valid to some extent, we must see things from the perspective of the whole system. Because the construction of data centers is a site project, with a view to realizing certain functions or meeting some customer requirements. A single device or simple patchwork of devices are doomed to failure. We must see the bigger picture, that is, considering the matching, coordination, and correlation amongst various devices, and design and install likewise to meet that requirement eventually.

## Slide 14: Power Supply System (1)
High-voltage power transformation and distribution system: Converts the 6 kV/10 kV/35 kV three-phase mains to 380 V/400 V three-phase mains and distributes power for downstream low-voltage devices.
DG system: As the backup power source, the DG system instantly supplies power to downstream devices once the mains power fails. There are low-voltage and medium-voltage DGs.
Automatic transfer switch (ATS) system: Automatically switches between one mains and the other and between the mains and the DG.

## Slide 15: Power Supply System (2)
Low-voltage distribution system: distributes the upstream electric energy to various electrical equipment, such as the uninterruptible power system (UPS), air conditioner, and lighting equipment, based on requirements, standards, and specifications.
UPS system: purifies and backs up electric energy, and provides pure and reliable power protection for IT loads.
UPS output power distribution system: distributes the UPS output electric energy to various IT equipment based on requirements and standards.
Rack power distribution system: distributes the electric energy inside the racks.
–48 V DC power supply: provides safe and reliable power supply for communication equipment.
Common power distribution architecture of data centers
Access-level power distribution
Room-level power distribution
Cabinet row-level power distribution
Mains
Diesel generator
UPS input PDF
Mains PDF
Modular UPS 1
Modular UPS 2
UPS output PDF 1
UPS output PDF 2
Precision air conditioner 1
Precision air conditioner 2
Precision air conditioner 3
Lightings, sockets, and other electrical equipment
Precision PDF 1
Precision PDF 2
Notes: In addition, the power supply and distribution system in a data center supplies and distributes power for the air conditioning, lighting, and other systems. It ensures the normal operation of the data center.

## Slide 16: Cooling System (1)
With the development of the society and the application of new technologies, the power consumption and power density of the data center increase significantly. The cooling system ensures that the equipment in a data center work in a proper environment.
Large sensible heat
Low latent heat
Large air volume and small enthalpy difference
Non-stop operation and perennial cooling
Multiple air flow modes
Plenum chamber air supply
Strict requirements for temperature, humidity, and cleanliness
Notes: A. Large sensible heat: The IT equipment and power devices in a data center dissipate heat through transferring, convection, and radiation, resulting in temperature rise in the equipment room. This type of heat is sensible heat. The heat dissipation capacity of a server cabinet ranges from thousands of watts to dozens of thousands of watts per hour, and the sensible heat ratio in the equipment room can reach 95%.
B. Low latent heat: Latent heat is energy that changes the humidity ratio in air but not change the temperature in the equipment room. There is no moisture dissipation equipment in the equipment room. The latent heat mainly comes from staff and outdoor air.
C. Large air volume and small enthalpy difference: Because of small latent heat in the equipment room, there is little humidity to be dehumidified. The temperature of air does not need to drop to below the dew point temperature before the air flows through the air conditioner evaporator. Therefore, the effective temperature difference and the enthalpy difference are small.
E. Multiple air flow modes: In data centers, the air flow mode is determined by heat source and its distribution characteristics, story height, equipment layout, and cables. Downflow, upflow, and regional air flow are the main air flow modes
F. Plenum chamber air supply: The air supply of air conditioners in the equipment room generally uses the space under the raised floor or above the ceiling for the plenum chamber air supply. The pressure stabilizing layer formed in the chamber ensures even air flow. The height of the plenum chamber should be lifted as high as possible.

## Slide 17
Notes: G. Strict requirements for temperature and humidity: Over temperature will lead to a higher equipment failure rate and lower reliability of servers and even equipment breakdowns. A high relative humidity may cause short circuits, corrosion, and condensation on equipment in the data center. Low relative humidity may generate electrostatic discharge (ESD) that affects equipment running.
H. Strict requirements for air cleanliness: There are strict requirements for air cleanliness in a data center. In a high-humidity environment, dust accelerates equipment corrosion and shortens its service life. In addition, accumulated dust on the heat sink increases the thermal resistance and reduces the heat exchange efficiency. Corrosive gases can quickly destroy metal films and conductors on printed circuit boards, resulting in increased resistance at terminations. Therefore, the air conditioning system for a data center must be equipped with efficient and proper filtering devices to filter out dust from the circulating air according to related standards.

## Slide 18: Cooling System (2)
Based on the scale and total capacity of data centers, there are now two prevalent solutions: air cooled cooling system and chilled water cooling system. In general, the chilled water solution is primarily used in extra large and large-sized data centers, and the air cooled solution is usually used in small- and medium-sized data centers.
500 m2
Equipment room scale
Chilled water
Building equipment room
Warehouse equipment room
Functional zoning for each floor
Independent room
Air cooled
Air cooled or chilled water
1000 m2
(2 MW)

## Slide 19: Cooling System (3)
Three cooling configurations: equipment room cooling, in-row cooling, and cabinet cooling.
In-cabinet
cooling
In-row air conditioner
In-cabinet air conditioner
In-room air conditioner
In-room
cooling
In-row
cooling
Notes: Selection of In-room, In-row, and Cabinet-level Cooling for Data Centers
  Cabinet-level cooling is the most flexible mode, can be deployed in shortest time, and supports the highest power density. However, extra expenditure is required.
  In-row cooling has many advantages similar to those of the cabinet-level cooling, for example, flexibility, deployment speed, and power density, and has a relatively low cost.
  In-room cooling can fast change the cooling distribution mode by configuring new perforated floors. In low-density data centers, all cabinets can share the cooling redundancy. This cooling mode has cost advantages and is also the simplest mode.

## Slide 20: Data Center Integrated Management (1)
Concept: The monitoring system in the equipment room implements central monitoring and maintenance management over the power and environment in the equipment room to improve the reliability of the data center and security of data devices, facilitate O&M, and increase management efficiency.
Objects: The power system, environment system, firefighting system, and security system are the primary objects to be monitored.
Functions: Based on the integrated network cabling system, the monitoring system in the equipment room adopts distributed monitoring, with the host placed in the monitoring room to run the software, to monitor all subsystems in a centralized manner using a uniform LCD. The monitoring system can monitor the operating status and parameters of all devices in real time, promptly generate alarms in forms of multimedia, voice, calls, and SMS when some components or parameters are abnormal, record historical data and alarms, and intelligently provide expert diagnosis, remote monitoring management, and web browsing.
Notes: Smart devices: Smart devices are monitored through communication ports (including RS232/422/485 bus serial and TCP/IP network communication ports). Smart devices include the UPS, master air conditioner, power meter, T/H sensor, ATS, chiller, and generator.
Non-smart devices: Non-smart devices are monitored through external smart meters or dry contacts. Non-smart devices include the security switch, power distribution switch, water leakage detection switch, and SPD.

## Slide 21: Data Center Integrated Management (2)

## Slide 22
Introduction to Data Center Development
Composition of Data Center Infrastructure
Introduction to Data Center Standards
Common Energy Consumption Indicators
Panorama of Huawei Data Center Solutions

## Slide 23: Overview of Data Center Standards
Standards are a way to unify the language and reduce communication costs. They are designed to make things simpler.
General standards
  Code for Design of Data Centers (GB 50174-2017)
  Data Center Site Infrastructure Tier Standard – Operational Sustainability
  Data Center Site Infrastructure Tier Standard – Topology
  TIA-942-B-2017, Telecommunication Infrastructure Standard for Data Centers, USA
Data center standards
National standards
Direct standards
Related standards
Industry standards
Association standards
Policy guidelines
Notes: There are many data center standards. Different countries have different standards. Only some standards are listed here.
GB 50174-2017 is the main reference standard for data center design and construction in China.
Tier standards are released by the Uptime Institute and are mainly used for Uptime Institute certification services. To obtain Uptime Institute certification, design, construction, and O&M must comply with Tier standards.

## Slide 24: Introduction to Uptime Tier Standards
The Uptime Institute is a well-known data center standards organization and an independent certifier. Uptime Tier certification consists of three parts: Tier Certification of Design Documents, Tier Certification of Constructed Facility, and Tier Certification of Operational Sustainability.
According to the Uptime Tier standards, data center infrastructure is classified into four levels:
  Tier I: Basic Data Center Site Infrastructure
  Tier II: Redundant Site Infrastructure Capacity Components
  Tier III: Concurrently Maintainable Site Infrastructure
  Tier IV: Fault Tolerant Site Infrastructure

## Slide 25: Introduction to TIA-942 Standard
TIA-942-B-2017 is Telecommunications Infrastructure Standard for Data Centers released by the USA. It classifies data centers into four classes based on the usefulness and security of infrastructure. Its appendix describes the technical requirements of the four classes for telecommunications, architectural infrastructure, electrical, and mechanical infrastructure.
  I Data Center: Basic
  II Data Center: Redundant Component
  III Data Center: Concurrently Maintainable
  IV Data Center: Fault Tolerant
Notes: TIA: Telecommunications Industry Association is an important industry association in the global communications and information technology industry.
At the beginning of 2000, the Uptime Institute authorized the TIA committee to use the Tier concept. In the first version of TIA-942-2005, data centers were classified into four tiers: Tier 1, Tier 2, Tier 3 and Tier 4. In 2013, the Uptime Institute canceled the Tier authorization. Later, data centers are classified into four classes: I, II, III, and IV according to TIA standards.

## Slide 26: Introduction to Other Standards (1)
  ISO/IEC 30134 series standards, including five volumes
    Overview and general requirements - 2016
    Power usage effectiveness (PUE) - 2016
    Renewable energy factor (REF) - 2016
    IT equipment energy efficiency for servers (ITEE) - 2017
    IT equipment utilization for servers (ITEU_SV) - 2017

## Slide 27: Introduction to Other Standards (2)
EU EN 50600 series standards
  By 2017, the European Committee for Electrotechnical Standardization (CENELEC) of the European Union (EU) has released the EN 50600 series standards, which include four parts in 10 standard texts. The EN 50600 series standards specify three levels of systems for availability, physical security, and energy efficiency implementation. It also provides requirements and suggestions on data center operation, processes and management.
Japan JDCC FS-001 standard
  Based on the TIA-942 standard, the JDCC FS-001 standard classifies data centers into four levels. It is also supplemented and modified based on the actual situation of Japan. The JDCC FS-001 standard incorporates the unique elements of Japan, including earthquake risk and assessment, reliability of commercial electric power, and products of high efficiency, and reliability.

## Slide 28
Introduction to Data Center Development
Composition of Data Center Infrastructure
Introduction to Data Center Standards
Common Energy Consumption Indicators
Panorama of Huawei Data Center Solutions

## Slide 29: Data Center Power Consumption (1)
Precision air conditioner
IT device
Humidifier
Chiller
PDU
UPS
Lighting and other devices
Power input
Switch/DG
Heat dissipation
Cooling system
IT device
Others
Power consumption of data centers includes the IT device loads, cooling device loads, lighting loads, and device power losses.
Because the power consumption of IT devices is difficult to reduce and that of the cooling system is the lion's share, lowering the power consumption of the cooling system is the key to improve the energy efficiency of the data center.

## Slide 30: Data Center Power Consumption (2)
Main sources of the data center energy consumption include the IT devices, lighting system, air conditioner, and power and distribution system. A lot of enterprises and scholars across the world made significant research in the data center energy consumption. Though the results differ in the exact proportion of each factor, the factors that constitute the energy consumption and the order of these factors by importance are largely the same.

## Slide 31: Power Consumption Index - PUE
Power usage effectiveness (PUE) is a widely-used comprehensive indicator inside and outside China that measures the data center infrastructure efficiency (DCiE). The formula is: PUE = PTotal/PIT, where PTotal indicates the total power consumption of the data center and PIT indicates the power consumption of the IT devices.
PUE | DCiE | Energy Efficiency Level
3.0 | 33% | Extremely poor
2.5 | 40% | Poor
2.0 | 50% | Average
1.5 | 67% | Good
1.2 | 83% | Excellent
PUE=
PTotal/PIT
DCiE = PIT/PTotal
Notes: In essence, the PUE is used to calculate how much power of the total power supplied to the data center is actually applied to the IT devices. The PUE ranges from 1.0 to infinity. The greater the PUE value of the DC equipment room, the more the power consumed by the DC infrastructure, such as the cooling and power supply. The PUE is easy to be defined and calculated. Measure the total power consumption of the data center and that of the IT devices respectively, you can immediately calculate the PUE of the entire data center.
The total power consumption of the data center indicates all power consumption required to maintain the normal operation of the data center, including the power consumption of the IT devices, cooling devices, power supply and distribution system, and other facilities. If the building where lies the data center is also for office running and other purposes, the power consumption incurred by office running and others must not be included in the total power consumption of the data center. In data centers, only power consumed by the IT devices is regarded as meaningful power.

## Slide 32: Power Consumption Index - pPUE
Partial PUE (pPUE) is an extension to the PUE concept and used to evaluate and analyze the energy efficiency of part of the data center or devices.
Before the pPUE is performed, the data center should be divided into different zones. The zone can be an equipment room in a multi-story data center building or a container module in a container data center.
pPUE is used to represent the energy efficiency of some zones or devices, and can be greater or less than the PUE. Generally, to improve the overall efficiency, we must first ameliorate the efficiency of devices or zones with greater pPUE values in the data center. pPUE is applicable to the partial energy efficiency evaluation of modular data centers built based on containers or other modular units, or large-sized data centers composed of many buildings and equipment rooms.

## Slide 33: Power Consumption Index - CLF/PLF
CLF is short for cooling load factor and PLF power load factor. CLF is used to represent the ratio between the power consumption of the cooling devices and that of the IT devices. PLF is used to represent the ratio between the power consumption of the power and distribution system and that of the IT devices.
CLF and PLF are supplements and extensions to PUE. Calculating CLF and PLF can help you analyze in a detailed manner the respective energy efficiency of the cooling system and power and distribution system.

## Slide 34: Power Consumption Index - RER
Renewable energy ratio (RER) is used to measure the utilization of renewable sources to renew the solar energy, wind energy, and hydro energy, and promote the use of carbon-free or low-carbon sources. In general, renewable energy indicates recyclable energy sources in nature, such as the solar energy, wind energy, hydro energy, biomass energy, geothermal energy, and ocean energy. Renewable energy sources are environment-friendly in use, widely distributed, and can be exploited locally. Fossil fuels, such as coal, oil, and gas, and nuclear energy constitute the counterpart of renewable energy.
In particular, RER is a new indicator proposed at the China Cloud Computing Promotion and Policy Forum in light of the fast growth of renewable energy sources in China. Now, RER is submitted to The Green Grid (TGG), an internationally-renowned organization that commits itself to improving the IT efficiency, for discussion.

## Slide 35
Introduction to Data Center Development
Composition of Data Center Infrastructure
Introduction to Data Center Standards
Common Energy Consumption Indicators
Panorama of Huawei Data Center Solutions

## Slide 36: Panorama of Huawei Data Center Solutions
NetCol5000-A/C
In-row precision air conditioner
(11–80 kW)
NetCol8000-A/C
In-room precision air conditioner
(50–253 kW)
FusionModule2000
Small and medium data center
2–48 IT cabinets, ≤ 250 kW
Air-cooled, ≤ 500 m2 (recommended)
FusionDC1000A
Small outdoor prefabricated all-in-one data center
4–8 IT cabinets, 8–52 kW
FusionModule500
Micro data center
1–2 IT cabinets, ≤ 3 kW
FusionDC1000B
Large and medium outdoor prefabricated modular data center
18–84 IT cabinets, > 100 kW
FusionModule800
Small data center
1–8 IT cabinets, 3–15 kW
FusionModule5000
Medium and large data center
6–48 IT cabinets, ≤ 250 kW
Chilled water, > 500 m2 (recommended)
UPS5000
(25–800 kVA)
UPS2000
(1–20 kVA)
Power distribution unit (PDU)
iBattery
Intelligent battery monitoring
NetEco 6000
management system
FusionPower5000
(1.2 MVA)
NetCol8000-E
Indirect evaporative cooling system
220 kW
Notes: Huawei provides a full series (small to large data centers) of FusionModule data center facility solutions for industries, enterprise digital transformation, and data center service providers. In addition, Huawei also provides solutions of UPS and cooling for key equipment in industries (such as manufacturing and rail transportation).

## Slide 37
(Single)Which of the following belong to the power supply system?
  UPS
  CCTV
  Access control system
  Cable tray
(Single)Which of the following is not an energy consumption indicator of a data center?
  PUE
  pPUE
  RER
  PFC
Notes: Answers:
  A
  D

## Slide 38
Introduction to Data Center Development
Composition of Data Center Infrastructure
Introduction to Data Center Standards
Common Energy Consumption Indicators
Panorama of Huawei Data Center Solutions

## Slide 39
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 41
Course Code
HCIA-DCF
V2.0
V2.0
Guo Bian/wx337261
2017.04.11
Lishaofeng/l00486775
Type
Wang Cong/wx760444
2020.04
Lishaofeng/l00486775
Notes: 2015.7.4
  调整版权和页码对齐，位于参考线8.5到8.9之间。
  调整编辑框行距为单倍行距。
2015.7.9
  删除此页课程版本后的“ISSUE”。
  新增“产品版本”和“课程版本”的示例。
2015.8.3
  调整母板主体和备注，段落格式为“允许标点溢出边界”。
2015.8.4
  删除缩略语页；
  重命名版式“8#空白”为“8#仅标题”。
2015.9.2
  新增备注模板，备注页正上方添加页眉，显示本章标题。
2015.9.14
  删除“谢谢”那页的白色“谢谢”。
2017.11.8
  调整母版中标题宽度。
2017.12.8
  适当拉长了备注页文本框长度，防止2013版后的PPT会自动换页。