## Slide 1
1.0
1.0
V2R0
V1R1
Guo Bian/wx337261
2017.05.04
Li Shaofeng/00486775
New
Wang Pulin/wx763618
2020.04.02
Li Shaofeng/00486775
Update
Update
Update
Update
Notes: 2015-07-04
  Aligned the copyright and page number and placed them between reference lines 8.5 and 8.9.
  Adjusted the line spacing of the edit box to a single line spacing.
2015-07-09
  Deleted the ISSUE column from this page.
  Added the examples of Product Version and Course Version.
2015-08-03
  Adjusted the main body and remarks of the master page and set the paragraph format to "Allow Punctuations to Cross the Boundary."
2015-08-04
  Deleted the acronyms and abbreviations.
  Changed the format name 8#blank to 8#title only.
2015-09-02
  Added a remark template and add a header on the top of the remarks page to display the title of this chapter.
2015-09-14
  Deleted the white Thank You from the Thank You page.
2017-11-08
  Adjusted the title width in the master page.
2017-12-08
  Lengthened the text box on the note page to prevent page break in PowerPoint 2013 and later versions.

## Slide 2: Basic Knowledge of Power Distribution

## Slide 3
After learning this course, you will be able to:
  Understand the basic concepts of power distribution
  Know the grounding system
  Know the common power distribution products

## Slide 4
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
Common Grounding Systems

## Slide 5: What Is Power Distribution?
Electrical system
Low-voltage (LV) electrical equipment
Definition
Requirement
Function
Transmission
Power distribution
Protection
Control
Monitoring
Power distribution
IEC, UL
Industry standards
Enterprise standards
Notes: The power distribution system consists of power distribution substations, high-voltage (HV) power distribution lines, power distribution transformers, LV power distribution lines, and corresponding control and protection equipment.
LV electrical equipment: equipment used for connection, disconnection, protection, control, or adjustment in circuits with 50/60 Hz AC, rated AC voltage of 1000 V or below, and rated DC voltage of 1500 V or below. LV electrical equipment mainly includes: the circuit breaker, load switch, disconnector, fuse, leakage protector, contactor, surge protective device (SPD), plug and socket, cable, and so on.
Power distribution: an electrical system that consists of LV electrical equipment for power transmission, distribution, protection, control, and monitoring
The power distribution design provides protection and control functions, such as short circuit protection, overcurrent protection, as well as connection and disconnection control.
The power distribution design improves maintenance, safety, protection, and EMC performance.
Power distribution standards: IEC, UL, GB, industry standards, and enterprise standards

## Slide 6: Data Center Distribution System
Generator
Generator distribution
L-voltage distribution
Auxiliary facilities
UPS
PDF
IT load
PDF for Cooling
Cooling system
RPDU
Power gird
H-voltage distribution
Transformer
Notes: Auxiliary facilities including security, lighting, elevators, etc.
This panorama shows the power distribution structure of the data center in IT scenarios. In addition, CT scenarios are also available. That is, DC power supply is used for loads and DC power supply is used for devices

## Slide 7: Low-Voltage Electrical Devices
Level.A： ACB
Level.B ： MCCB
Level.C ： MCB
IT load
Notes: 通过低压电气设备。

## Slide 8
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
Common Grounding Systems

## Slide 9: Power Supply
Dual power supplies: A load has two power supplies, which are considered independent of each other for safety.
Emergency power supply system: To ensure personal safety, the emergency power supply system protects the environment and other equipment from being damaged.
Emergency power supply (power supply for safety facilities): It serves as a part of the emergency power supply system.
  In data centers, it means power supply for emergency lights, fire pumps, and other safety equipment.
Standby power supply: When the normal power supply is powered off, the standby power supply is used to maintain the power supply required by the equipment for non-safety reasons.
  The standby power supply can be a generator set or a dedicated feed loop independent of the normal power supply.
Notes: The dual power supplies may be power supplies from different power grids, and may be two different HV loops. When either power supply is abnormal, the other one can still supply power without interruption.
Emergency power supply system: a power supply system that maintains the operation of electrical equipment and electrical devices to avoid damage to the environment and other equipment

## Slide 10: Power Supply Requirements
Uptime Institute Uptime specifies the power supply reliability requirements of data centers of different levels.
Data Center Tier | Tier IV | Tier III | Tier II | Tier I
Overall function requirement | Fault tolerance (one fault), active-active power supply and distribution routes | Planned online maintenance, active-standby power supply and distribution routes | One power supply and distribution route | One power supply and distribution route
Mains input requirement | / | / | / | /
DG requirement | 2N is recommended, but N+1 can also be used. | N+1 | N+1 | N
UPS requirement | 2N | N+1 | N+1 | N
Backup time requirement | Meeting DG startup requirements | Meeting DG startup requirements | Meeting DG startup requirements | Meeting DG startup requirements
DG fuel storage requirement | 12 hours | 12 hours | 12 hours | No specific requirements

## Slide 11: Voltage
The power grid transmits 110 kV, 35 kV, 20 kV, and 10 kV power to enterprises. Then the transformer decreases the voltage to 380 V, and the LV power distribution system transmits the power to the power-consuming equipment in data centers.
When 220 V/380 V single-phase power-consuming equipment is connected to a three-phase system, it is recommended that the three phases be balanced.
For the 220 V load supplied by the LV power grid, if the line current is less than or equal to 60 A, the 220 V single-phase power supply can be used. When the line current is greater than 60 A, the 380 V three-phase four-wire power supply is recommended.
Single-phase, two-wire
Three-phase, four-wire
Single-phase, three-wire

## Slide 12: Load Characteristics: Resistor, Capacitor, and Inductor
Resistors have the function of blocking current and can be used as electric heating parts to convert electric energy into internal energy. It is marked as R or r, and the unit is ohm.
Capacitors are two unconnected plates used to store and discharge electric charges, converting electrical energy into electric field energy. It is marked as C, and the unit is F.
Inductors are spiral coils, in which a changing magnetic field is generated by changing a current, and the magnetic field is prevented from converting electric energy into magnetic energy by changing a magnetic flux. It is marked as L, and the unit is H.
R
Z
C
L
R: Resistor
L: Inductor
C: Capacitor
Z: Impedance
Impedance vector diagram
Notes: When the load is a pure resistance load, the power factor is 1.
When the load contains inductors, the current lags the voltage by 90°.
When the load contains capacitors, the current leads the voltage.

## Slide 13: Power
There are three kinds of power supplied to the load by the power supply: active power, reactive power, and apparent power.
  Active power (P): the power that can convert electric energy into other forms of energy and can be directly consumed
  The formula for calculating the power of a three-phase circuit is as follows: P = √3UIcosφ
  Reactive power (Q): When the load contains inductors or capacitors, the equipment generates reactive power. Equipment such as transformers and motors require the magnetic field generated by reactive power to work. Therefore, reactive power is not useless.
  The formula for calculating the power of a three-phase circuit is as follows: Q = √3UIsinφ
  Apparent power (S): the sum of active power P and reactive power Q
  The formula for calculating the power of a three-phase circuit is as follows: S2 = Q2 + P2 = √3UI
Notes: When the load is a pure inductive or capacitive load, φ = 90°, sinφ = 1. Therefore, Q = UI, that is, only reactive power is consumed and active power is not consumed. When the load is a pure resistance load, φ = 0°, sinφ = 0. Therefore, Q = 0, that is, only active power is consumed and no reactive power is required.
When there are too many non-linear loads, the power factor of the power grid is too low to meet related requirements. In this case, capacitors need to be connected in parallel or in series to improve the power factor. For example, in an inductive load loop, if the active power is 90 kW and reactive power is 30 kW, the power factor needs to be increased to 0.9. In this case, the target reactive power is 10 kVar, the reactive power to be compensated is 20 kVar, and a 20 kVar capacitor compensation device can be connected in parallel.
Power distribution transformers and motors can convert and transmit energy only by creating alternating magnetic fields. Therefore, reactive power is not useless, but its power is not converted into mechanical energy or thermal energy. Therefore, in the power supply and consumption system, both active power supply and reactive power supply are required.

## Slide 14: Power Quality and Harmonic
Power quality: refers to the voltage quality, that is, the quality of the voltage amplitude, frequency, and waveform. The main technical specifications include harmonic, voltage deviation, power supply interruption, three-phase voltage imbalance, and voltage fluctuation and flicker. The ideal power quality means the sinusoidal voltage with constant power and constant amplitude, as well as continuous power supply.
Power quality issues may cause great loss to data centers. Common power quality issues of data centers include harmonic, voltage deviation, and power supply interruption.
We will focus on these three issues this time.
Notes: The data center carries core IT equipment and information data of enterprises. Any fault may bring great risks to customers. Therefore, the data center must meet the requirements for power supply quality, surge protection, and grounding of IT equipment to ensure that a stable and reliable modern computer room is constructed to better meet the future service development of enterprises.

## Slide 15: Power Quality and Harmonic
Harmonic: In the AC power grid, the voltage and current waveforms of much non-linear electrical equipment are not complete sine waveforms. The part that is the same as the industrial frequency (50 Hz) is the fundamental wave. The wave whose frequency is a multiple of the fundamental wave frequency (greater than 1) is the harmonic wave.
Harmonic diagram
Notes: Harm of harmonics: The computer system in a data center is sensitive to voltage fluctuation. Harmonic may cause serious consequences such as damage to sensitive components, information loss, and disk program flushing.

## Slide 16: Voltage Deviation
The voltage deviation is the relative deviation of the operating voltage to the nominal voltage of the power supply and distribution system under normal operating conditions. The value is expressed in percentage:
100%.
U
: voltage deviation percentage, 100%
: operating voltage (V)
: nominal voltage of the system (V)
Notes: In an LV power distribution system, when selecting cables, ensure that the current-carrying capacity of the cables meets the requirements and the line voltage drop meets the equipment requirements. The line voltage drop is the product of the current and impedance of the line. The value is expressed in percentage. Generally, the engineering design deviation does not exceed 5%.
The line reactance consists of impedance and inductive reactance. For details, see the product manual of the manufacturer or the Code for Design of Low Voltage Electrical Installations.
The voltage deviation should be the voltage difference of the entire loop from the power supply to the terminal of the power-consuming equipment.

## Slide 17: Power Supply Reliability
Power supply reliability: refers to the continuous power supply capability of a power supply system.
The electric energy of a data center is mainly from the power grid. The power supply reliability of the power grid directly affects the power supply system architecture (power supply configuration and battery configuration) of the data center. The mains power supply reliability is classified into the following types.
Type | Power Outage Times (Times/Year) | Power Outage Duration (Hours/Times)
Class 1 power supply | ≤ 12 | ≤ 0.5
Class 2 power supply | ≤ 42 | ≤ 6
Class 3 power supply | ≤ 54 | ≤ 8
Class 4 power supply | Seasonal long-time power outage occurs or no mains is available. | 
Notes: Unavailability: the average value of instantaneous availability in a given time range in a stable state. It is evaluated based on the number of outage times and outage duration.
(Source: GB/T 2900.13-2008 Electrotechnical terminology -- Dependability and quality of service and IEC 60050 (191): 1990)

## Slide 18
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
  Abstract
  Conversion Equipment
  Control Equipment
  Auxiliary Materials
  Common Grounding Systems

## Slide 19: LV Power Distribution Equipment
Definition
  Based on the usage requirements and control signals, the LV power distribution equipment can connect and disconnect the circuits with the rated voltage of 1000 V AC or 1500 V DC or below using one or more components manually or automatically to control, adjust, convert, detect, and protect the controlled objects in the circuit.
Common equipment
  Conversion equipment: transformer and diesel generator (DG)
  Control equipment: power distribution frame (PDF), circuit breaker, and fuse
  Auxiliary materials: cables
Notes: Primary electrical equipment refers to the electrical equipment directly used in the production, conversion, transmission, diversion, distribution, and use of electric energy. It includes generators, transformers, circuit breakers, disconnectors, automatic switches, knife switches, buses, transmission lines, power cables, and so on.
Primary equipment: conversion equipment, control equipment, protection equipment, and compensation equipment
Secondary electrical equipment refers to the LV electrical equipment that monitors, controls, adjusts, and protects the primary equipment, provides operating conditions, or delivers production command signals for operation and maintenance personnel.
It includes control switches, relays, control cables, instruments, signal equipment, automatic devices, and so on.

## Slide 20
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
  Abstract
  Conversion Equipment
  Control equipment
  Auxiliary materials
  Common Grounding Systems

## Slide 21: Transformer
A transformer consists of an iron core and two or more coils (windings) with different numbers of turns wound around the iron core.
In a data center, the transformer converts the 10 kV/20 kV voltage on the power grid side into 400 V voltage for equipment.
Common transformer types:
  Common oil-immersed transformer: applies to substations in normal environments.
  Dry-type transformer: applies to places with high fireproof requirements or substations in damp and dusty environments.
Transformer
Transformer structure
Notes: A group of coils connected to the AC power supply is called the primary winding, and the other group connected to the load is called the secondary winding. The two windings are not electrically connected.
Transformer ratio: If the number of turns of the primary winding is N1 and the number of turns of the secondary winding is N2, the voltage ratio is N1/N2 and the current ratio is N2/N1. An ideal transformer does not have power loss during voltage conversion. Primary side power: U1 x I1 = U2 x I2.
A transformer uses electromagnetic induction to transfer AC power and signals and can be used as a voltage converter, current converter, and impedance converter, or used for electrical isolation.
Common transformer brands: ABB, Siemens, Schneider, and Tebian Electric Apparatus

## Slide 22: DG
A DG is a combination of a diesel engine and a generator (usually an AC generator) to generate power in cases of a mains outage
The DG starts and burns diesel fuel to convert chemical energy into power, ensuring normal operation of the data center.
The whole set is generally composed of a diesel engine, generator, control box, fuel tank, battery for starting and controlling, protection equipment, emergency cabinet, and so on.
DG
Diesel engine
Heat sink
Control box
Notes: Diesel engine: converts the chemical energy of fuel into the mechanical energy of the rotor.
Generator: converts the mechanical energy of the rotor to power.
Control box: controls and protects the diesel engine and generator.

## Slide 23
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
  Abstract
  Conversion Equipment
  Control equipment
  Auxiliary materials
  Common Grounding Systems

## Slide 24: LV PDF
The rated current of the LV PDF is 50 Hz AC. The power distribution system with a rated voltage of 380 V is used as the driving force for power conversion and control for lighting and power distribution.
The LV PDF should adapt to the rated circuit value and installation conditions. The basic features are as follows:
  Rated operating voltage
  Rated frequency
  Rated operating current
  Indoor and outdoor types, Ingress protection (IP) rating
  Fixed type or drawer type
Notes: The rated voltage of a common LV PDF is 380 V or 660 V, the rated frequency is 50 Hz, and the current is determined based on the load.
Based on the application environment, PDFs are classified into indoor PDFs and outdoor PDFs. The dustproof and waterproof level of outdoor PDFs is IP54 or higher, which is applicable to outdoor environments. The PDF uses an AC air conditioner, heat exchanger, or semiconductor air conditioner and a direct-ventilation unit for heat dissipation to keep the cabinet temperature at a constant value. Cables, rubber strips, and thermal insulation foam used in the PDF are made of flame retardant materials. Do not use indoor PDFs in outdoor scenarios.

## Slide 25: IP Rating
IP rating refers to the protection level of protecting electrical equipment against intrusion of foreign objects. IP rating consists of two digits. The first digit indicates the level of protection against dust and foreign object intrusion. The second digit indicates the level of protection against moisture and water intrusion. The larger the value, the higher the protection level.
IPXX
Dustproof
Waterproof
Digit | Dustproof Range | Description
0 | No protection | There is no special protection against people or objects outside.
1 | Prevents intrusion of solid objects with a diameter of greater than 50 mm. | Prevents human bodies (such as palms) from contacting internal electrical parts due to accidents and prevents large foreign objects (with a diameter greater than 50 mm) from intrusion.
2 | Prevents intrusion of solid objects with a diameter of greater than 12.5 mm. | Prevents fingers from contacting internal electrical parts and prevents medium-sized foreign objects (with a diameter greater than 12.5 mm) from intrusion.
3 | Prevents intrusion of solid objects with a diameter of greater than 2.5 mm. | Prevents tools, wires, and similar small objects whose diameter or thickness is greater than 2.5 mm from contacting internal electrical parts.
4 | Prevents intrusion of solid objects with a diameter of greater than 1.0 mm. | Prevents tools, wires, and similar small objects whose diameter or thickness is greater than 1.0 mm from contacting internal electrical parts.
5 | Prevents foreign objects and dust. | Prevents foreign objects from intrusion. Although dust cannot be completely prevented, the dust does not affect the normal operation of electrical equipment.
6 | Prevents foreign objects and dust. | Prevents foreign objects and dust from intrusion.
Notes: Common HV PDFs are IP40-rated, LV PDFs are IP30-rated, and outdoor PDFs are IP54-rated or higher.

## Slide 26: IP Rating
Digit | Waterproof Range | Description
0 | No protection | There is no special protection against water or moisture.
1 | Prevents droplets from intrusion. | Vertical droplets (such as condensed water) do not cause damage to electrical equipment.
2 | When the equipment is tilted by 15 degrees, droplets can still be prevented. | When the electrical equipment is tilted by 15 degrees, droplets do not damage the equipment.
3 | Prevents sprayed water from intrusion. | Prevents rain or damage caused by water sprayed in the direction less than 60 degrees from the vertical angle.
4 | Prevents splashing water from intrusion. | Prevents splashing water in all directions from intruding into electrical equipment and causing damage.
5 | Prevents water jets. | Prevents water jets from all directions from the nozzle from intruding into the electrical equipment and causing damage.
6 | Prevents large waves from intrusion. | Prevents damage caused by the invasion of large waves for electrical equipment installed on the deck.
7 | Prevents water intrusion during immersion. | Ensures that the electrical equipment is not damaged due to water immersion when electrical equipment is immersed in water for a certain period of time or the water pressure is below a certain standard.
8 | Prevents water intrusion during sinking. | Ensure that no damage is caused by water immersion when the electrical equipment sinks indefinitely under specified water pressure.
Notes: Common HV PDFs are IP40-rated, LV PDFs are IP30-rated, and outdoor PDFs are IP54-rated or higher.

## Slide 27: Low-Voltage Circuit Breakers
Function:
  Switch
  Overload protection
  Short circuit protection ( instant /short delay )
Classification:
  ACB (Air Circuit Breaker)
  MCCB (Mould Case Circuit Breaker)
  MCB (Miniature Circuit Breaker)
  HY-MAG (Hydraulic-pressure Magnetic Circuit Breaker)
  RCD (Residual Current Device)

## Slide 28: Low-Voltage Circuit Breakers - ACB
Definition:
  The type of circuit breaker, which operates in air (where air-blast as an arc quenching medium) at atmospheric pressure, is known to be an Air Circuit Breaker.
Application and Uses:
  Used for main power distribution in large industrial plant.
  Used for protection of transformers, capacitors and generators.
  Carry heavy current (thousands of amperes).
  Intelligent monitoring functions: remote control, alarms and data transmission.
Notes: The working principle of Air Circuit breaker is rather different from other types of circuit breaker. The main aim of circuit breaker is to prevent reestablishment of arcing after current zero where the contact gap will withstand the system recovery voltage. It does it same work, but in a different manner. During interruption of arc, it creates an arc voltage instead of supply voltage. Arc voltage is defined as the minimum voltage required for maintaining arc .

## Slide 29: Low-Voltage Circuit Breakers - MCCB
Definition:
  MCCB is a type of electrical protection device that is commonly used when load currents exceed the capabilities of miniature circuit breakers.
Features:
  Used in industrial areas widely.
  carry medium current (hundreds of amperes).
  High breaking capability (Icu Ics).
  operated rapidly.
  The tripping devices are interchangeable and adjustable.
  Intelligent monitoring functions: catenation, remote control,
  alarms and data transmission.
Notes: Tripping current is adjustable
alarm when overload, short circuit, or inner fault
Data transmission can be realized by communication module with modbus protocol to other devices.

## Slide 30: Low-Voltage Circuit Breakers - MCB (1)
Definition:
  An MCB or miniature circuit breaker is an
  electromagnetic device that embodies complete
  enclosure in a molded insulating material.
Main parameters:
  Carry miniature current (from 1 A to 100 A usually)
  Nearest to the loads
  Rated voltage Un：230V/400Vac, 60Vdc
  Rated breaking current Icu：4.5kA，6kA，10kA…
  Characteristic: B, C or D
  Tripping principle: Thermal-Magnetic tripping（TM）
Notes: An MCB or miniature circuit breaker is an electromagnetic device that embodies complete enclosure in a molded insulating material. The main function of an MCB is to switch the circuit, i.e., to open the circuit automatically when the current passing through it exceeds the value for which it is set. It can be manually switched ON and OFF as similar to normal switch if necessary

## Slide 31: Low-Voltage Circuit Breakers - MCB (2)
Tripping Characteristics
  Definition:
    B, C, D according to IEC 60898
    Z, K according to IEC 60947-2
  Application:
    Characteristics Z (2-3) In
    Characteristics B (3-5)In
    Characteristics C (5-10) In
    Characteristics D (10-20)In
    Characteristics K (8 –15)In
  Characteristic C is suggested for the MCB in the ICT loads scenario.
Notes: X axis indicates tripping current, it is times of rated current. Y axis indicates the tripping time. top half of the curve stand for thermal tripping ,used as overload protection, tripping time is relatively long, as heating is a slow procedure, start point is 1.45In, as current increase, the tripping time become shorter, it is an inverse time curve. The bottom part of the curve stand for magnetic tripping, used for short circuit protection. The middle vertical line stand for trip setting value, in the middle is C type, its trip setting is (from 5 to 10) In ，match the need of low voltage power distribution. B type (3-5)In, is used for the load with small short current, such as household appliance. D (10-20)In, is used for the load with big starting current. Such as motors.
K type trip setting (8 –15)In，suitable for motor protection. Because its thermal tripping start from 1.2In, but B/C/D type is 1.45In, suitable for motor overload protection. D type used with motor protection，need to add thermal relay for overload protection.
Z type (2-3) In, for the protection of loads such as semiconductor devices or measuring circuits using current transformers.
Thermal Trigger Q=I2Rt,Magnetic Trigger F=BIL

## Slide 32: Low-Voltage Circuit Breakers - RCD
Principle:
  Kirchoffs Law: ∑I=0
  Earth leakage current protector
Classification:
  By Principle:
    Electromagnetic type
    Electronic type
  By over current protection:
    Residual Current Circuit Breaker (RCCB)
    Residual current Circuit Breaker with Over-current protection (RCBO)
  By relay time: instant type, selected type
RCCB
Magnetic type RCD

## Slide 33: Transfer Switch
Definition:
  A transfer switch is an electrical switch that switches a load between two sources.
Classification:
  ATS: Automatic Transfer Switch ( Mechanical action )
  STS: Static Transfer Switch ( SCR )
Types
  Open transition
  Closed transition
  Soft loading
Notes: Automatic transfer switch (ATS) can divided into CB (over current protection)and PC(No over current protection )
An Automatic Transfer Switch (ATS) is often installed where a backup generator is located, so that the generator may provide temporary electrical power if main source fails. (<100ms)
Static transfer switch (STS)
A static transfer switch uses power semiconductors such as Silicon-controlled rectifiers (SCRs) to transfer a load between two sources. Because there are no mechanical moving parts, the transfer can be completed rapidly, perhaps within a quarter-cycle (<10ms)of the power frequency.
Phase Poles :2 (L,N), 3(L1,L2,L3), 4(L1,L2,L3,N)

## Slide 34: Fuse
Definition:
  Widely applied in low voltage distribution and control systems
  One key short-circuit protection device for a single electrical equipment.
Classification:
  Based on the breaking range: g (for full range breaking) and a (for partial breaking)
  Based on the classification: G (common fuse) and M (for motor circuits)
Feature parameters:
  Rated voltage
  Rated current
  Rated breaking capability
  Time-Current feature
Fuses
Holders
Pullers
Notes: classification：D (delay)，N（Non-delay）R (rectifier protection) L cable protection
Breaking capability normally hundreds of K amperes, greater can MCB(several K amperes).

## Slide 35: Disconnector
Definition
  It is mainly used to isolate the power supply, transfer switching, and connect and cut off the small-current circuit. It has no arc extinguishing function.
Feature
  During electrical equipment maintenance, the disconnector can provide an electrical interval, which is a visible disconnection point.
  The disconnector cannot be operated with load. It can be operated only when the circuit breaker is disconnected.
Classification by structure
  Knife switch
  Fuse-type knife switch
  Classification by operation mode
  Manual disconnector
  Automatic disconnector
Knife switch
Fuse-type knife switch
Automatic disconnector
Notes: When repairing electrical equipment, cut off the power supply to separate the maintained part from the live part and keep an effective isolation distance.

## Slide 36: SPD (1)
Definition
  SPD is installed at the front end of equipment to protect the equipment from being damaged by overvoltage or overcurrent caused by external cables.
Feature
  Protection level: level I, II, and III, or class B, C, and D
  Maximum discharge current Imax: maximum single shot current the SPD can handle without getting damaged
  Nominal discharge current In: through-current capability that enables the SPD to endure surge
  Rated impulse voltage value : resistance capability that enables the SPD to prevent overvoltage
  Residual voltage: peak voltage between SPD terminals when the discharge current passes through
Notes: The lightning protection level is determined based on the interception efficiency of the SPD or the importance, use nature, and value of the electronic information system.
Phase electrodes use varistors (disconnected after being broken down), and ground electrodes use gas discharge tubes (conductive after being broken down).
Rated shock resistance voltage: 6 kV for equipment at the input end of the power cable, 4 kV for power distribution branch circuit equipment, and 2.5 kV for power-consuming equipment
Nominal current: peak value of the maximum impulse current that can pass the SPD within a specified number of times and a specified waveform without causing any substantial damage to the SPD
Impulse current : 10/350 μs through the SPD. The amount of electric charge (Q) passing through the SPD within 10 μs should be equal to 50% of the amplitude current.
雷电防护等级按照防雷装置拦截效率或电子信息系统的重要性、使用性质，价值确定。
相极使用的是 压敏电阻（击穿以后是断开的），接地极使用的是 气体放电管 （击穿以后是导通的）。
耐冲击电压额定值：电源进线端设备/6kV，配电分支电路设备/4kV，用电设备2.5kV
标称电流：SPD不发生实质性破坏，而能通过规定次数，规定波形的最大限度的冲击电流峰值
冲击电流𝐼_𝑖𝑚𝑝：流过SPD的10/350μs,其在10μs内通过的电荷量Q应等于幅值电流的50%

## Slide 37: SPD (2)
Impulse current and nominal current of the SPD
Lightning Protection Level | General Power Distribution Box (PDB) |  | Branch PDB | Equipment Room PDB
 | Class 1 test | Class 2 test | Class 2 test | Class 2 test
 | (kA) | (kA) | (kA) | (kA)
B | ≥ 15 | ≥ 60 | ≥ 30 | ≥ 5
C | ≥ 12.5 | ≥ 50 | ≥ 20 | ≥ 3
D | ≥ 12.5 | ≥ 50 | ≥ 10 | ≥ 3
Lightning Protection Level | General Power Distribution Box (PDB) |  | Branch PDB | Equipment Room PDB
 | Class 1 test | Class 2 test | Class 2 test | Class 2 test
B | ≥ 15 | ≥ 60 | ≥ 30 | ≥ 5
C | ≥ 12.5 | ≥ 50 | ≥ 20 | ≥ 3
D | ≥ 12.5 | ≥ 50 | ≥ 10 | ≥ 3
Notes: The larger the nominal current and impulse current of the SPD, the better the performance of the SPD.

## Slide 38
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
  Abstract
  Conversion Equipment
  Control equipment
  Auxiliary materials
  Common Grounding Systems

## Slide 39: Introduction to Power Cables
The basic structure of a power cable consists of the core (conductor), insulation layer, shield layer, and protection layer.
Copper, aluminum, and aluminum alloy are usually used as cable conductors. Copper conductors are recommended for data center cables.
Cables can be classified into DC cables and AC cables based on the power system.
Basic cable features:
  Cable type
  Rated operating voltage
  Insulating material
  Conductor type
  Cross-sectional area
Notes: For details about cable types, see the Code for Design of Low Voltage Electrical Installations, Code for Cable Design of Electric Engineering, or manuals provided by manufacturers.

## Slide 40: Naming Rules for Power Cables
No. | Meaning | Value
1 | Type code | ZRC: class C flame retardant
2 | Conductor | L: aluminum; T: copper
3 | Insulation layer code | YJ: crosslinked polyethylene; V: PVC sheath
4 | Protection layer code | V: PVC sheath
5 | Armored layer code | 0: none; 2: double steel belt; 3: thin steel wire
6 | Number of cable cores | 3: three-core cable
7 | Cross-sectional area | 120: 120 mm²
ZRC L – YJV 22 -3×120mm²+ 1×70mm²
1
3
6
7
5
4
2
6
7
Notes: Aluminum alloy cable: YJHLV
Type: flame-retardant cable, fire-resistant cable, and other types. Select based on environment requirements.
Conductor: The electrical conductivity and reliability of copper are higher than those of aluminum. For materials with the same cross-sectional area, the current-carrying capacity of copper is larger.

## Slide 41
Power Distribution System Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
Common Grounding Systems

## Slide 42: Grounding System Overview
Concept
  Grounding is to connect the grounding terminals of electrical equipment or communication equipment to the ground through grounding devices and inject the electric charges of the grounding terminals into the ground for the purpose of working or protection. In this way, the dangerous voltage is reduced and electromagnetic interference is prevented.
  Components of the grounding system
  Types and functions of grounding
Notes: In a telecommunication bureau (station), grounding plays an important role. It is not only related to the safety of equipment and maintenance personnel, but also directly affects the quality of communication. Therefore, it is of great significance to master the basic knowledge of grounding and to choose and maintain the grounding equipment correctly.

## Slide 43: Components of the Grounding System
The grounding device consists of all grounding bodies and grounding leads. The grounding system is formed by connecting the grounding devices to the grounding terminals of the electrical equipment through the ground cable.
Ground conductor
Ground lead
Ground bar
Ground cable
Ground bar of the power distribution panel
Busbar to the communications equipment room
Ground branch cable
Ground terminal of the equipment

## Slide 44: Grounding Types
Function
Functional grounding
Functional and protective grounding
Grounding for purposes other than electrical safety
Protective ground
For safety purposes, ground the system or equipment at one or more points.
Protective grounding of electrical equipment: The exposed conductive parts of electrical equipment are grounded, for example, the shells of the UPS and PDF are grounded.
Operating grounding: ground the live parts that have been powered off.
Lightning protection and grounding: SPD (such as lightning rod and overvoltage protector)
ESD grounding: ground the static electricity, such as the grounding of flammable and explosive pipes and electronic components.
Grounding of the power system: ground the power system according to the operation requirements of the system. For example, ground the neutral point of the AC power system and the positive pole of the DC power system.
Signal circuit grounding: ensures that signals have stable reference potentials.
Grounding that improves the electromagnetic compatibility of equipment, including functional grounding (anti-interference) and protective grounding (anti-damage)
Load
AC system grounding
DC system grounding

## Slide 45: Earthing system Introduction
Definition：
  To connect the metallic (conductive) Parts of an Electric appliance or installations to the earth (ground) is called Earthing. IEC 60364 distinguishes three families of earthing arrangements, using the two-letter codes TN, TT, and IT.
The first letter indicates the connection between earth and the power-supply equipment (generator or transformer):
  "T" — Direct connection of a point with earth (Latin: terra)
  "I" — No point is connected with earth (isolation), except perhaps via a high impedance.
The second letter indicates the connection between earth and the electrical device being supplied:
  "T" — Earth connection is by a local direct connection to earth (Latin: terra), usually via a ground rod.
  "N" — Earth connection is supplied by the electricity supply Network, either as a separate protective earth (PE) conductor or combined with the neutral conductor.
Classification: TN( TN-C, TN-S,TN-C-S,) 、IT、TT.
Notes: In other words, to connect the metallic parts of electric machinery and devices to the earth plate or earth electrode (which is buried in the moisture earth) through a thick conductor wire (which has very low resistance) for safety purpose is known as Earthing or grounding.

## Slide 46: Earthing system Introduction - TN (1)
Definition：
  In a TN earthing system, one of the points in the generator or transformer is connected with earth, usually the star point in a three-phase system. The body of the electrical device is connected with earth via this earth connection at the transformer.
Classification：
  TN−S：PE and N are separate conductors that are connected together only near the power source. This arrangement is a current standard for most residential and industrial electric systems particularly in Europe.
  TN−C：combined PEN conductor fulfills the functions of both a PE and an N conductor.
  TN−C−S：combined PEN conductor from transformer to building distribution point, but separate PE and N conductors in fixed indoor wiring and flexible power cords.
Notes: In other words, to connect the metallic parts of electric machinery and devices to the earth plate or earth electrode (which is buried in the moisture earth) through a thick conductor wire (which has very low resistance) for safety purpose is known as Earthing or grounding.
TN networks[edit]
In a TN earthing system, one of the points in the generator or transformer is connected with earth, usually the star point in a three-phase system. The body of the electrical device is connected with earth via this earth connection at the transformer.
The conductor that connects the exposed metallic parts of the consumer's electrical installation is called protective earth (PE; see also: Ground). The conductor that connects to the star point in a three-phase system, or that carries the return current in a single-phase system, is called neutral (N). Three variants of TN systems are distinguished:

## Slide 47: Earthing system Introduction - TN (2)
TN-S
TN-C-S
TN-C
Notes: TN−S：PE and N are separate conductors that are connected together only near the power source. This arrangement is a current standard for most residential and industrial electric systems particularly in Europe.
TN−C：combined PEN conductor fulfills the functions of both a PE and an N conductor.
TN−C−S：combined PEN conductor from transformer to building distribution point, but separate PE and N conductors in fixed indoor wiring and flexible power cords.

## Slide 48: Earthing system Introduction - TT
Definition：
  The TT system : Technique for the protection of persons: the exposed conductive parts are earthed and residual current devices (RCDs) are used.
  Operating technique: interruption for the first insulation fault.

## Slide 49: Earthing system Introduction - IT
Definition：
  In an IT network, the electrical distribution system has no connection to earth at all, or it has only a high impedance connection.

## Slide 50
Which of the following is the most common grounding system in a data center?
A. TN-S
B. TN-C
C. TN-C-S
D. TT
E. IT
Notes: Answers:
  C

## Slide 51
Data Center Power Distribution Overview
Basic Concepts of the Power Distribution System
Common LV Electrical Equipment
Common Grounding Systems
Introduction to Data Center Digital Power Products

## Slide 52
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Popular Tools
Support Web
Enterprise APP
Support APP