## Slide 1: Basic Knowledge of UPS
Notes: UPS: Uninterruptible power supply

## Slide 2
The chapter describes UPS basic knowledge, including the function and work principle of UPS and the common configuration solution.

## Slide 3
On completion of this course, you will be able to:
  Know the basic function of UPS;
  Know the basic working mode of UPS;
  Know the common configuration solution of UPS.

## Slide 4
What Is a UPS
Huawei UPS Solutions
Common Configuration Solutions
Typical Application Scenarios

## Slide 5: UPS Development History
First generation:
Dynamic storage UPS Before 1985
Second generation:
Analog control transformer-based UPS
1985–2000
Third generation:
IGBT rectification-supported
Transformer UPS
2000–2006
Fourth generation:
Full-digital high-efficiency modularized UPS Since 2007
Notes: First generation: Efficiency: 50%–60%; Key components: flywheel or generator; Control mode: analog control.
Second generation:1985–2000; Efficiency: < 88%; Key components: silicon controlled rectifier (SCR); Control mode: analog control.
Third generation: 2000–2006; Efficiency: 92%–94%; Key components: insulated gate bipolar transistor (IGBT) and metal-oxide semiconductor (MOS); Control mode: semi-digital UPS.
Fourth generation: Since 2007; Efficiency: > 96%; Key components: MOS (IGBT)+digital signal processing (DSP); Control mode: full-digital, redundant, and dual-bus.
An uninterruptible power supply (UPS) is an energy conversion device that uses the battery chemical energy for backup to supply uninterruptible power when power failures, such as mains disconnection or exceptions, occur.

## Slide 6: Why Is the UPS Required?
Power grid pollution affects network and device security.
  Power interruption, voltage fluctuation, transient peak currents, voltage surges, and high-voltage pulses which damage servers, routers, and disk arrays.
  Harmonic distortion, high-frequency interruption, and frequency drifts which substantially increase the bit error rate (BER) and decrease the data transmission rate.
Nine power grid faults

## Slide 7: UPS Functions
Power purification
Stable AC outputs
Uninterruptible power supply
Power management
Solving the problem of power grid pollution
  Increases the input power factor, decreases harmonic pollution to the power grid, and supplies pure power to loads.
Solving the problem of mains outage
  When the mains fails, batteries in the UPS supply power to loads.
Solving the problem of mains voltage fluctuation
  The UPS supports a wide input voltage range, which ensures stable outputs for loads when the mains voltage fluctuates.
Solving the problem during AC power maintenance
  As an important power supply device, the UPS can be monitored by the network management system (NMS), ensuring easy maintenance.

## Slide 8: UPS System Classification
By structure:
  Offline UPS;
  Line-interactive UPS;
  Online UPS.
By capacity:
  Small-sized UPS (< 20 kVA);
  Medium-sized UPS (20 kVA to 200 kVA);
  Large-sized UPS (> 200 kVA).
By installation method:
  Tower-mounted UPS;
  Rack-mounted UPS.

## Slide 9: Composition of an UPS
Notes: UPSs are classified into off-line UPSs, line-interactive UPSs, and double-conversion UPSs. Currently, double-conversion UPSs are mainly used.
Double conversion: AC-DC-AC conversion, purifying mains input

## Slide 10: Main Function Units of the UPS – Rectifier
Functions of the rectifier
  Converts AC power into DC power.
  Implements power factor correction (PFC) and voltage boosting.
  Reduces the pollution to the power grid.
Notes: The rectifier is a circuit that converts AC power into DC power to provide stable DC power for the downstream inverter. In addition, the input power factor is adjusted to a value closer to 1, which reduces the pollution to the power grid.

## Slide 11: Main Function Units of the UPS – Inverter
Functions of the inverter module
  Converts DC power into AC power.
  Converts DC power from batteries into AC power.
  Provides pure AC power by high-speed operation of switching diodes.
Notes: The inverter is a circuit that converts DC power into AC power.
During a mains outage, the inverter converts the DC power supplied by batteries into AC power for loads. It also converts DC power from the boost circuit of the upstream rectifier into pure AC power for loads by high-speed operation of switching diodes.

## Slide 12: Main Function Units of the UPS – Bypass Module
Functions of the bypass module
  Internal bypass: When the main converter becomes faulty or fails to work properly, the UPS automatically transfers to internal bypass mode.
  The maintenance bypass isolates the UPS to ensure safety and power continuity during maintenance.
Notes: Internal bypass: When the main converter becomes faulty or fails to work properly, for example, due to overtemperature or overload, the UPS can switch to internal bypass mode automatically and manually.
Maintenance bypass: It is used to separate one or more power circuits of the UPS to ensure security and/or power continuity of loads during maintenance. When the maintenance bypass is enabled, the main power supply or backup power supply can supply power to loads. In this case, loads are not protected.
Focus on the differences between the two.

## Slide 13: Main Function Units of the UPS – Charger
Functions of the charger
  Charges batteries when the AC input is normal.
Notes: Batteries supply DC power to the inverter to ensure continuous power supply when a mains outage occurs.
Typically, the battery voltage is 2 V, 6 V, or 12 V. UPSs often use 12 V batteries. Batteries are connected in serial or parallel to provide required DC current and backup capacity.

## Slide 14: UPS Working Modes – Classification
The UPS has five working modes:
  Normal mode
  Battery mode
  Bypass mode
  Maintenance mode
  Economy control operation (ECO) mode

## Slide 15: Online UPS - Normal Mode
DC/AC
Inverter
Mains input
UPS output
Static bypass
AC/DC
rectifier
Maintenance bypass
Bypass input
Battery string
In normal cases, the UPS works in inverter mode (normal mode);
In this mode, the mains supplies power to customers' loads using rectifiers and inverters;
UPS supplies power to the batteries using chargers.

## Slide 16: Online UPS - Battery Mode
If the mains supply fails or exceptions occur, the UPS immediately switches to the battery mode.
In this case, batteries supply power to customers' loads using inverters.
After the mains recovers, the UPS immediately switches back to the normal mode.
Mains input
UPS output
Bypass input
DC/AC
Inverter
Static bypass
AC/DC
rectifier
Maintenance bypass
Battery string

## Slide 17: Online UPS - Bypass Mode
If a UPS is faulty, it immediately switches to the bypass mode (static bypass mode) for power supply;
In this case, the bypass power source supply power to customers' loads through the static bypass.
DC/AC
Inverter
Static bypass
AC/DC
rectifier
Maintenance bypass
Battery string
Mains input
UPS output
Bypass input

## Slide 18: Online UPS - Maint. Mode
When a faulty UPS is maintained, the UPS must be manually switched to the maintenance bypass mode.
DC/AC
Inverter
Static bypass
AC/DC
rectifier
Maintenance bypass
Battery string
Mains input
UPS output
Bypass input

## Slide 19: Online UPS – ECO Mode
In this mode, if the bypass voltage and frequency are in the specified range, the UPS supplies power to loads over the bypass. If the bypass voltage and frequency are outside the range, the UPS transfers to normal or battery mode.
DC/AC inverter
Mains input
UPS load
Static bypass
AC/DC
rectifier
Maintenance bypass
Bypass input
Battery

## Slide 20: UPS Key Parameters (1)
Capacity
  The UPS loading capability can be indicated by the apparent power (kVA) or active power (kW), for example, 200 kVA or 180 kW. Since output capacitors of inverter units generate reactive power, the active power value cannot exceed the apparent power value.
Output power factor
  The output power factor indicates the UPS capability for carrying loads with active power. Generally, the output power factor is 0.7, 0.8, 0.9, or 1.
Efficiency
  Under the same customers' loads, higher UPS efficiency leads to less UPS loss and operating expense (OPEX). In normal cases, efficiency of medium- and large-sized UPSs is higher than 0.9.

## Slide 21: UPS Key Parameters (2)
Input voltage and frequency range
  If the input voltage and frequency range is wide, the UPS is adaptable to poor power grids. When the input voltage and frequency exceed the threshold, the UPS switches to the battery mode. A wide voltage range reduces the number of battery discharge times and therefore prolongs the battery lifespan.
Overload capability
  The high overload capability ensures power supply quality. If the UPS overloads, it works in normal mode for a short period and then switches to the static bypass mode. If overload persists, the UPS shuts down.
Input current harmonic
  The low total distortion of the input current waveform (THDi) reduces pollution to the power grid.

## Slide 22: Rack&Tower - mounted UPS
Rack-mounted UPS
Tower-mounted UPS
Can be placed in a standard 19-inch cabinet;
Provides a 20 kVA power capacity or lower;
Enables customers to use rack-mounted batteries.
Can be placed on the ground or desk;
Provides a power capacity of 0.5 kVA to 1500 kVA, capacity higher than 3 kVA is placed on the ground.

## Slide 23: Modularized UPS
Power module
The modularized design facilitates capacity expansion and prevents excessive investment in initial construction.
The redundancy design increases reliability and availability.

## Slide 24
What Is a UPS
Huawei UPS Solutions
Common Configuration Solutions
Typical Application Scenarios

## Slide 25: Huawei UPSs
UPS2000-A/G series
(1–10 kVA/1–20 kVA)
UPS5000-A series (30–800 kVA)
FusionPower series
1600 kVA
Integrated UPS5000-E
(50–125 kVA)
UPS5000-E/S series (50–800 kVA)

## Slide 26: UPS2000-G Small-sized UPS Solution
UPS2000-G:
1 kVA to 20 kVA
Introduction
  N+X redundancy and single UPS configuration based on different reliability requirements;
  Power backup time from 10 minutes to 2 hours and an intelligent management solution;
  Network-wide monitoring platform.
Advantages
  High reliability and efficiency, ensuring power supply continuity and reducing the OPEX;
  Intelligent battery management, prolonging the battery lifespan;
  Network-wide monitoring platform, improving system maintainability and reducing the OPEX.
Notes: Application scenarios
  Customer service centers
  Offices NMS servers
  Access devices

## Slide 27: L and M-sized UPS5000-A Solution
Introduction
    N+X redundancy and dual-bus configuration based on different reliability requirements;
    Power backup time from 10 minutes to 2 hours;
    Compatible with the NetEco.
Advantages
    High reliability and efficiency, protecting investment and reducing the OPEX;
    Flexible configuration, meeting different requirements;
    Intelligent battery management and network-wide monitoring platform, improving system maintainability.
Notes: Application scenarios
  Equipment rooms of data centers, such as the IDC
  Central equipment rooms

## Slide 28: L and M-sized UPS5000-E/S Solution
UPS5000-E-(50–200 kVA)
Introduction
    Modularized design, enabling smooth capacity expansion with load increasing;
    N+X redundancy and dual-bus configuration based on different reliability requirements;
    Network-wide monitoring platform, covering all power supply facilities.
    Advantages
    High efficiency and modularization, preventing low-efficiency power system running as services increase in initial construction;
    Network-wide monitoring platform, improving system maintainability and reducing the OPEX.
Notes: Application scenarios
  Key equipment, such as routers, charging servers, and value-added servers in core equipment rooms
  IT equipment in key convergence equipment rooms and switching rooms.
  Advantage: Flexible configuration and strong expansion capability, meeting different requirements.

## Slide 29: FusionPower
Introduction
  Integrates the UPS input and output cabinets and UPS, and achieves a system efficiency of 97%.
  Uses the iPower intelligent technology to improve system reliability and reduce O&M costs for customers.
  Adopts the all-in-one design to effectively reduce the power distribution workload, as well as save footprint and installation time.
Feature
  The redundancy design for all modules improves reliability. Visualized monitoring of all links improves O&M efficiency.
  The iBattery monitors the battery status to eliminate fire risks.
  High efficiency at low load: The efficiency is higher than 96% when the load rate ranges from 20% to 50%, saving electricity fees.

## Slide 30
What Is a UPS
Huawei UPS Solutions
Common Configuration Solutions
Typical Application Scenarios

## Slide 31: Single UPS System
ATS: automatic transfer switch
PDF: power distribution frame
Single UPS system advantages
    Simple configuration and low cost;
    High running efficiency.
Single UPS system disadvantages
    The usability is limited. If the UPS is faulty, loads are powered in bypass mode, and the power supply quality cannot be guaranteed;
    During UPS, battery, or power distribution device maintenance, the load power supply quality cannot be guaranteed;
    No redundant system exists. When the UPS is faulty, loads are lack of protection;
    Multiple single point failures exist.
Notes: A single UPS system meets the power supply requirements to key loads. N indicates the number of UPSs required for minimum power supply.

## Slide 32: Redundant Parallel or N+1 System
N+1 system advantages
  The N+1 system can properly run if a UPS is faulty, which has higher reliability than the N system;
  The system design is simple with low costs.
N+1 system disadvantages
    UPSs used in an N+1 system must be of the same design, manufacturer, rated specifications, technique, and configurations;
    Single point failures exist in inputs and outputs of the N+1 system;
    If a single UPS and its downstream devices (except for batteries) are maintained, loads cannot be protected;
    The UPS load ratio and the operation efficiency is low.
Notes: Redundant parallel system configuration solution.
  When a UPS is faulty, key loads do not need to be powered in bypass mode.
  Outputs of multiple UPSs with the same capacity in a parallel system can be converged.
  Communications cables are required to connecting UPSs in a parallel system to ensure output phase and amplitude synchronization between UPSs.

## Slide 33: Dual-Bus Redundancy System
Single input load
Dual input load
Dual-bus system advantages
    Two independent power supplies are available, preventing single point failures and providing powerful fault tolerance;
    The system provides comprehensive input and output redundant configuration;
    UPSs, batteries, and other power distribution devices can be maintained without transferring loads to the bypass mode.
Dual-bus system disadvantages
    Redundancy design, leading to high costs;
    Low load ratio and low efficiency.
Notes: Dual-bus system
  No single point failure
  High reliability and cost

## Slide 34
Working Principles
Huawei UPS Solutions
Common Configuration Solutions
Typical Application Scenarios

## Slide 35: UPS Application
  Data center;
  Business hall;
  Self-service terminal.
Finance
Government
  Data center;
  Monitoring center;
  E-government.
Energy
  Scheduling center;
  Monitoring center;
  Data center;
  Data center for short message service.
Transportation
  Communications scheduling center;
  Data center;
  Basic power supply system.
Manufacturing
  Control center;
  Data center;
  Office system.
Retail
  Data center;
  Billing system;
  Logistic scheduling center.
ISP
  IDC;
  E-office system;
  Basic power supply system.
  Data center;
  Central equipment room;
  Site equipment room;
  Customer service center.
Communications

## Slide 36: UPS Load Types
IT equipment
    Server and storage device
    Switch and router
    Terminal
    ATM
Data center
Enterprise network equipment room
System control center
Automated production line
Household acoustics
Office
Industrial facilities
    Industrial control system
    Automated production line
    Precision instrument
Personal use
    PC
    Household appliance such as acoustics

## Slide 37: Scenario (1) - Large-sized IDC
Important loads, such as servers and storage devices, require reliable power supply systems.
Large- and medium-sized equipment rooms require the UPS capacity of 300 kVA or higher and power backup time from 10 minutes to 2 hours.
Notes: The system must be smoothly upgraded in the future.
An intelligent remote monitoring solution must be provided to ensure uninterruptible power supply in an integrated manner.
Image Source: http://3ms.huawei.com/multimedia/docMaintain/mmMaintain.do?method=showMMDetail&f_id=img202008220107

## Slide 38: Scenario (2) - NMS
M2000
N2000
T2000
U2000
Input
UPS
Input PDF
High load importance requires a reliable power supply system.
NMSs require that UPSs be fast deployed, easily installed and maintained, and transferred between tower-mounted and rack-mounted.
Notes: NMSs require the UPS capacity of 1 kW to 10 kW and power backup time of 1 hour.
NMSs feature abundant ports, easy maintenance, and simple cable routing.

## Slide 39: Scenario (3) - Centralized Equipment Room
UPS 1
UPS 2
Server
Midrange computer
Firewall
Input
Input PDF
Output PDF
Disk array
High service importance requires a reliable power supply system.
Provincial centralized equipment rooms require the UPS capacity of 60 kVA to 200 kVA and more than 1 hour power backup time.
The UPSs must be applicable to multiple types of loads and servers and meet efficiency and energy conservation requirements.
Notes:   The input and output power distribution frames (PDFs) must have liquid crystal displays (LCDs).
  Image Source: http://3ms.huawei.com/multimedia/docMaintain/mmMaintain.do?method=showMMDetail&f_id=img202008150401

## Slide 40
(Short Answer Question)Why do we need UPS ?
(Short Answer Question)What is the benefit of module UPS?
(Short Answer Question)Which configuration solution is used at your site?
Notes: 1、Power grid pollution affects network and device security.
2、The modularized design facilitates capacity expansion and prevents excessive investment in initial construction；The redundancy design increases reliability and availability.
3、N,N+1 or 2N?

## Slide 41
The chapter describes UPS basic knowledge, including the function and work principle of UPS and the common configuration solution.

## Slide 42
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 44
LiShaofeng/ 00178216
2015.10.8
New
HCIA-DCF
Wang Congsai/wx277162
2016.11.21
Li Shaofeng/00486775
Updated
Guobian/wx337261
2016.12.12
Li Shaofeng/00486775
Chenkaifeng/cwx377854
2017.04
Li Shaofeng/00486775
WangCong/wx760444
2020.4
Li Shaofeng/00486775
Notes: 2015.7.4
  调整版权和页码对齐，位于参考线8.5到8.9之间。
2015.7.14
  新增更多信息和推荐的样例。
2015.8.3
  胶片主体和备注页，段落设置为“允许标点溢出边界”。
2015.8.4
  删除缩略语页。
2016.12.12
  P26 名称更换