## Slide 1: Basic Knowledge of Huawei DC Power Systems

## Slide 2
DC power systems are widely used in communication base stations and some data center CT scenarios. The slides describe the basic knowledge of Huawei –48 V DC power systems.
Notes: Control, protection, and automatic reclosing of substations (220 V), emergency lighting (220 V), DC oil pumps (12/24 V), cameras (12 V), and base stations (48 V)
Indoor distribution system: The signal of a mobile base station is uniformly distributed in every corner of a room by using an indoor antenna distribution system, so that an indoor area has desirable signal coverage.

## Slide 3
Upon completion of this course, you will be able to understand the main functions of Huawei DC power systems, understand the architecture and basic composition of DC power systems, and master the basic knowledge of DC power system battery management.

## Slide 4
Abstract
Architecture and Components
Battery Management
Application Scenarios
Huawei DC Power Systems

## Slide 5: DC Power System Application Scenarios
AC power (mains) and its direction change periodically as time changes.
DC power and its direction do not change with time. It is steady current.
DC power is used for powering electronic devices, and AC power is used for upstream electric energy transmission.
DC arcs are more difficult to be extinguished than AC arcs. Unless otherwise specified, do not mix AC and DC devices.
0
t/s
U/V
380
DC power
220
AC power
Notes: Compared with DC power, AC power has the following advantages:
Can be boosted by a transformer to reduce the power transmission loss.
Applicable to AC motors.

## Slide 6: Basic Functions of Huawei DC Power Systems
Two basic functions
  Rectification
    Converts 220 V AC or 380 V AC power into –48 V DC power.
    Provides redundancy for rectifiers.
  Battery management
    Manages the charge and discharge of batteries connected in parallel on the output side. That is, batteries can be charged and discharged with appropriate voltages, currents, and modes to ensure that the DC load operates uninterruptedly when the AC power failure occurs.

## Slide 7: Output Voltage
Why is the polarity negative?
  Due to historical reasons, the positive pole of the telecom power supply was grounded at the early stage, forming a loop through the ground and saving cables.
  The positive grounding can reduce the corrosion of negative devices.
Why is the voltage –48 V?
  The early-stage power systems use the original lead-acid batteries, and the voltage is a multiple of the basic (single battery) voltage 1.2 V.
  According to the device component and line capabilities, 48 V voltage is selected to ensure the communication distance of local calls and security.

## Slide 8: Logical Composition
The telecom power system consists of the AC power distribution unit (PDU), DC PDU, rectifier, and monitoring unit.
AC
PDU
Rectifier
Rectifier
Rectifier
DC
PDU
Monitoring module
Mains input
Battery
string
1
Battery
string
2
Local operation
FSU
Remote monitoring
Standby AC output
CAN communications cable (or RS485)
–48 V DC
Notes: Controller Area Network (CAN) is one of the most widely used field buses in the world. CAN is a serial communication bus to effectively support distributed real-time control with high security level.
Field supervision unit (FSU): The FSU is a bridge between the supervision end office and the supervision center. As the core of data processing for the entire supervision system, the FSU collects raw data from collectors of the end office, and sends the processing result to the supervision service station and server. The FSU also receives control commands from the supervision service station to control devices in the end office.
The mains enters the rectifiers through the AC PDU. The rectifiers convert AC power into –48 V DC power and the power enters the DC power distribution frame. The power is then supplied to communications devices.
Typically, the system runs in parallel floating charge state. That is, rectifiers and batteries work in parallel. Rectifiers supply power to communications devices and provide float charge current for batteries. When the mains is cut off, rectifiers stop working and the batteries power the devices to ensure the normal operation of the devices. After the mains recovers, rectifiers power the devices again and charge batteries.

## Slide 9
Abstract
Architecture and Components
Battery Management
Application Scenarios
Huawei DC Power Systems

## Slide 10: Physical Architecture
Basic components
  AC PDU
    AC input, AC output, AC surge protective device (SPD), and line protection
  Rectifier
    Converts AC power into DC power (high-frequency switch rectification).
  DC PDU
    DC junction, output, SPD, load power-off, and battery protection
  Monitoring unit
    Measures AC and DC power distribution signals; manages, controls, and monitors rectifiers; analyzes and outputs alarms; manages loads and batteries.
DC PDU
Monitoring unit
AC PDU
Rectifier

## Slide 11: Electrical Conceptual Diagram
Electrical conceptual diagram
AC PDU
Monitoring unit
Rectifier
DC PDU
Notes: BLVD: battery low voltage disconnection
LLVD: load low voltage disconnection

## Slide 12: Rectifier Parameters
Input
  Input voltage range
  Input frequency range
  Power factor
Output
  Output voltage adjustment range
  Output current adjustment range
  Regulated voltage precision
Notes: Power factor: The rectifier adjusts the power factor of the input current.
Regulated voltage precision: ratio of the actual output voltage to the designed output voltage. For example, if the designed output voltage is 5 V and the actual output voltage is 5.01 V, the regulated voltage precision is 0.2% (0.01/5 x 100%).

## Slide 13
Abstract
Architecture and Components
Battery Management
Application Scenarios
Huawei DC Power Systems

## Slide 14: Working Principle
Monitoring parameters
Input parameters
Control intervention process
Float charge voltage
Pre-output
voltage of modules
Battery
temperature
Battery temperature
compensation
Battery equalized
charge
Battery test
Bus voltage
Current control
Battery charge
current
Final output

## Slide 15: Main Functions
Equalized charge and floating charge management:
  When the real-time battery capacity, charge current, and charge time meet certain conditions, the equalized charge and float charge modes switch with each other.
Battery disconnection protection:
  After an AC outage occurs or rectifiers become faulty, batteries start discharging and the battery voltage decreases. If the AC power does not recover when the battery voltage decreases to a certain extent, batteries need to be disconnected to prevent battery damage.
Temperature compensation:
  When the batteries are being charged, the temperature increases slowly. To ensure that the batteries work at a proper temperature, the battery charge voltage is decreased when the battery temperature is too high and the battery charge voltage is increased when the battery temperature is too low.

## Slide 16
Abstract
Architecture and Components
Battery Management
Application Scenarios
Huawei DC Power Systems

## Slide 17: Application Scenarios
DC power systems are widely used in communication base stations and some data center CT scenarios.
Air conditioner
Cabinet
Air conditioner outdoor unit
Battery rack
DC power system
Communication base station scenario
Data center CT scenario
Notes: The power distribution devices in the DC power supply system should be configured based on the long-term load.

## Slide 18: Position in the Power Distribution System
The mains enters the rectifiers through the AC PDU. The rectifiers convert AC power into –48 V DC power, and then the DC PDU distributes the power to DC devices.
ATS
AC
DC
Air conditioner
Battery
Inverter
AC load
DC load
DC power system
Notes: The power distribution devices in the DC power distribution system should be configured based on the long-term load.

## Slide 19
Abstract
Architecture and Components
Battery Management
Application Scenarios
Huawei DC Power Systems

## Slide 20: Huawei DC Power Systems
30 A
100–200 A
30–90 A
30–60 A
TP48200B
TP48200A
200–24, 000 A
ETP4830
ETP4890
TP4860H
ETP48200
100–200 A
100–200 A
TP48600B
TP483000D
100–300 A
TP48300B
TP4860C
30–60 A
100–600 A
TP482000B
100–10,000 A
Mini shelter
Rectifier efficiency: > 96%
Embedded power system
Wall-mounted power system
Outdoor power system
Indoor power system
CO power system
15 A
30 A
50 A
100 A
Notes: Huawei offers high-efficiency site power solutions ranging from 30 A to 24,000 A, including embedded, combinational, split-type, and wall-mounted power systems and mini shelters, meeting the requirements of indoor and outdoor communications networks. Huawei rectifier efficiency is higher than 96%. Huawei power systems have carrier-class reliability and support carriers' business development.

## Slide 21
(Short Answer Question)What are the basic functions of DC power systems?
(Short Answer Question)What are the basic components of a DC power system?
Notes: 1. Rectification and battery management.
1. AC PDU, DC PDU, rectifier, and monitoring unit.

## Slide 22
After learning this chapter, we are able to:
  Understand the telecom power.
  Understand the architecture and composition of DC power systems.
  Master the principles and features of DC power systems.

## Slide 23
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 25
Wang Pulin/wx763618
2020.12
Li Shaofeng/l00486775
New