## Slide 1: Basic Knowledge of Batteries

## Slide 2
On completion of this course, you will be able to:
  Understand the battery development and application in the ICT field.
  Get familiar with the classification and naming of batteries.
  Get familiar with the basic principles and structure of batteries.
  Understand the performance differences between lead-acid and lithium-ion batteries.

## Slide 3
Battery Overview
Lead-acid Battery
Lithium-ion Battery
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 4: History
French physicist Gaston Planté invented the (open-type) lead-acid battery.
1859
1957
Sonnenschein invented the gel battery.
Gates Corporation applied for the invention patent of the valve regulated lead acid (VRLA) battery.
1975
1992
The use of VRLA batteries increased significantly in Europe and the Americas.
In Asian countries, the telecommunications sector advocated the use of VRLA batteries.
1991
Sony released the first lithium-ion battery.
1994
Bellcore launched the lithium polymer battery for mobile phones.
Valence started commercial application of lithium iron phosphate (LFP) materials.
2004
Saft launched lithium-ion batteries for telecommunications.
2005
2010
The Nissan Leaf, equipped with lithium-ion batteries, was launched.
Notes: There are several important milestones in the development of batteries:
1. French physicist Gaston Planté invented the prototype of lead-acid batteries in 1859. The lead plate was immersed in sulphuric acid, and the battery worked in much the same way as modern batteries.
2. The selection of power batteries for the Apollo 15 Lunar Roving Vehicle enabled the development of lead-acid battery technology, such as the operating temperature and self-discharge control.
3. Gates Corporation invented the VRLA battery prototype.
4. VRLA batteries began to be widely used in the telecommunications industry worldwide.
Until now, absorbent glass mat (AGM) batteries have become an important part of the data center power system.

## Slide 5: Definition
A chemical battery, generally referred to as battery, is a device that converts chemical energy into electrical energy. After a battery is discharged, it can be recharged to regenerate the internal active substances, that is, to convert the electrical energy into chemical energy. It converts chemical energy into electrical energy again when it is discharged. This type of battery is called storage battery or secondary cell.
Main rechargeable batteries in the market include nickel metal hydride batteries, lead-acid batteries, lithium-ion batteries, and lithium polymer batteries.
Positive electrode/Graphite
Electrolyte
Negative electrode
Electrical energy
Chemical energy
Charging
Discharging
Lead-acid battery
Lithium-ion battery
Notes: Primary cell: also called galvanic cell. If the electrolyte in the primary cell does not flow, the primary cell is called dry cell. Because the battery reaction is irreversible or it is difficult to carry out reversible reactions, the battery cannot be recharged after being discharged. Zinc-manganese dry batteries, mercury batteries, silver-zinc batteries, and lithium batteries are all primary cells.
Secondary cell: also called storage battery. It is a type of battery that can be used repeatedly after being charged and discharged. Secondary cells include lead-acid batteries, lithium-ion batteries, nickel-cadmium batteries, nickel metal hydride batteries, sodium-sulfur batteries, sodium-nickel chloride batteries, and flow batteries.

## Slide 6: Function
Storage battery are sound DC power sources and are stable in voltage, free of fluctuation, and easy and reliable to use. Therefore, storage battery are widely used in the communications systems. Storage battery can be backup power sources for the AC UPS and DC power system, the startup power source, and the DC operation and control power source in the high-voltage power distribution system.

## Slide 7: Technical Specifications (1)
Rated capacity: refers to the nominal capacity, which indicates the minimum capacity that can be discharged according to standards or industrial standards.
Actual capacity: refers to the capacity that can be discharged after a fully charged battery is discharged to the specified end-of-discharge (EOD) voltage under certain discharge conditions. The unit is Ah or Wh.
  Discharge rate: For example, C10. C indicates the capacity, and 10 indicates the number of hours for the battery to discharge to the specified voltage at a certain current. The rated discharge current can be obtained by dividing the capacity by the number of hours.
  SOH: State of health, refers to the Percentage of actual capacity to rated capacity.
  SOC: State of charge, refers to the Percentage of current remaining capacity to actual capacity.
Notes: To set a unified condition, several discharge rates are set based on the battery structure features and usage. The most common discharge rates are 20-hour, 10-hour, and 2-hour (for UPS power systems), which are represented by C20, C10, and C2. C indicates the battery capacity, and the number following C indicates that the battery discharge capacity is related to the discharge current. Discharge capacity decreases as the discharge current increases.

## Slide 8: Technical Specifications (2)
Rated voltage: refers to the approximate value used to identify the voltage of a battery type. For example, the rated voltage of a single VRLA battery is 2 V.
Open-circuit voltage: refers to the terminal voltage of a battery in the open-circuit state. The open-circuit voltage of a battery is equal to the electric potential difference between the positive electrode and the negative electrode when the battery is open-circuited (that is, when no current passes through the two electrodes).
EOD voltage: indicates the voltage when a battery is used up. If the voltage decreases due to continuous discharging, the battery will be damaged. EOD voltage is the protection voltage set to prevent battery overdischarge. When the voltage reaches the value, the discharging should be terminated.
Notes: To set a unified condition, several discharge rates are set based on the battery structure features and usage. The most common discharge rates are 20-hour, 10-hour, and 2-hour (for UPS power systems), which are represented by C20, C10, and C2. C indicates the battery capacity, and the number following C indicates that the battery discharge capacity is related to the discharge current. Discharge capacity decreases as the discharge current increases.

## Slide 9: Technical Specifications (3)
Equalized charging: During the use of batteries, battery voltages are unbalanced due to the individual difference and temperature difference of batteries. To avoid the deterioration of this imbalance trend, the charge voltage of the battery string needs to be increased to activate the batteries. In this way, characteristics of each battery in the battery string are balanced.
Float charging: To balance the capacity loss caused by battery self-discharge, batteries need to be charged at a constant voltage for a long time.
Depth of discharge (DOD): indicates the percentage of battery discharge capacity to rated battery capacity. Generally, when the discharge capacity of a battery exceeds 80% of its rated capacity, it is considered that DOD is achieved.

## Slide 10: Application in Data Centers
In a data center, batteries are installed at the end of the UPS. When the mains fails, batteries supply DC power to the UPS, and the UPS converts the DC power into AC power required by loads to ensure continuous operation of devices.

## Slide 11
Battery Overview
Lead-acid Battery
  Overview
  Battery Structure
  Working Principle
Lithium-ion Battery
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 12: Definition
VRLA battery is a battery improved in material, structure, and process based on the common anti-acid and explosion-proof lead-acid storage battery.
The basic feature is that the battery does not need to be maintained by refilling acid or water during operation. Thanks to its sealing structure, the battery does not leak acid or exhaust acid smog.
On the battery cover is a one-way exhaust valve (safety valve), which automatically exhausts the excessive gas in the battery when the internal battery pressure increases to the threshold and automatically closes itself after the exhausting to avoid gas entry.

## Slide 13: General Category
Based on electrolyte: acid battery and alkaline battery
Based on electrolyte content: flooded battery and starved-electrolyte battery
Based on vent plug structure: open-type battery, vented battery, and acidapray-proof battery
Based on cell voltage: 2 V battery, 6 V battery, and 12 V battery
      Based on purpose: stationary battery, mobile battery, starter battery, traction battery, railway battery, motorcycle battery, coal mine battery, energy storage battery, and battery for other purposes

## Slide 14: Battery Classification in ICT
Lead-acid battery
Flooded lead-acid battery
Starved-electrolyte battery
AGM (Absorbed Glass Mat)
GEL (Gelled)
2 V
Common 12 V
12 V front access
2 V
2 V
Common 12 V
12 V front access
(Based on electrolyte content)
(Based on the storage method of electrolyte)

## Slide 15: Naming Rule
The model number of the lead-acid battery is composed of three parts. Part 1 indicates the number of storage battery in series; part 2 indicates the type and feature of the storage battery; part 3 indicates the rated capacity of the storage battery. Other codes can also be added on the right after the rated capacity if necessary.
Rated capacity
Feature
Type
Number of storage batteries in series
Part 1 Part 2 Part 3

## Slide 16: Examples
GFM-1000: a stationary valve-regulated sealed lead-acid battery, rated capacity 1000 Ah (common in ICT scenarios).
6-GFM-100: six stationary valve-regulated sealed lead-acid batteries in series, rated capacity 100 Ah (common in ICT scenarios).
6-Q-150: a lead-acid battery string of six batteries in series for startup, rated capacity 150 Ah.
No. | Battery Type (Purpose) | Code |  | No. | Battery Feature (Purpose) | Code
1 | Starter | Q |  | 1 | Sealed | M
2 | Stationary | G |  | 2 | Maintenance-free | W
3 | (Electric) Traction | D |  | 3 | Antiacid | F
4 | Valve-regulated | F |  | 4 | Gel electrolyte | J
5 | Energy storage | U |  | 5 | Air-tightness | Q

## Slide 17
Battery Overview
Lead-acid Battery
  Overview
  Battery Structure
  Working Principle
Lithium-ion Battery
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 18: Main Components
Take the most widely-used AGM lead-acid battery for example, its main components include the positive plate, negative plate, electrolyte, battery separator, battery chute, and other parts, such as the terminal, busbar, and safety valve.
Safety valve
Busbar
Positive plate
Battery separator
Negative plate
Battery chute
Notes: Due to the sealing requirements, the VRLA battery must not generate much gas during charging, only a very small amount of internal gas that cannot be consumed can be exhausted. So the VRLA battery, as illustrated in the following figure, is different from common lead-acid battery.

## Slide 19: Safety Valve
The safety valve is a key component of VRLA battery. The quality of the safety valve directly determines the lifespan, performance uniformity, and safety of the VRLA battery. The function of the safety valve is:
  To automatically exhaust the excessive gas in the battery to lower the internal battery pressure when the internal pressure increases to the threshold.
  Unidirectional exhausting means that air cannot enter the battery, which avoids battery self-discharge.

## Slide 20: Plate
The battery plate can be positive or negative. Battery plates are composed of active substances and plate grids, and there is a separator between the positive and negative plates, as shown in the following figures. Active substances for the positive and negative plates are lead dioxide (PbO2) and gray sponge lead (Pb) respectively.
Notes: Bus bars, also called connecting bars, are used to connect the same polar plates in the same battery to form a plate group, or connect the same type of batteries to form a metal lead bar of a battery group to perform connection and conduction.
Batteries can be connected on the battery cover or through the wall. The battery appearance is neat and neat.

## Slide 21: Separator
The battery separator has the following functions:
  Keeps the positive and negative plates insulated from each other.
  Absorbs electrolyte, and ensures that the electrolyte does not flow and that the negative plate is damp.
  Serves as the gas channel. Many holes in the battery separator facilitate the oxygen moving from the positive plate to the negative plate.
  Slows the disconnection of active substances.
Negative plate
Positive plate
Battery separator

## Slide 22: Battery Structure – Electrolyte
The electrolyte, composed of pure concentrated sulfuric acid and pure water, is absorbed in the separator to conduct electricity and participate in electrochemical reaction. The post terminal is the external terminal. The safety valve is used to unidirectionally adjust the internal pressure of the battery to prevent air from entering the battery.
H2SO4 molecular ball-and-stick model H2O molecular ball-and-stick model
In a VRLA battery, the electrolyte does not flow, that is, the electrolyte is absorbed by active substances on the plate and the separator film, and the saturation degree of the electrolyte is 60%–90%.
When the saturation degree of the electrolyte is lower than 60%, it indicates that the battery loses electrolyte seriously, and the active substances on the plate cannot fully contact the electrolyte. If the saturation is higher than 90%, the diffusion channel of the oxygen from the positive electrode is blocked by the electrolyte, which affects the diffusion of the oxygen to the negative electrode. In addition, the gel electrolyte does not flow.
Notes: The battery chute is used to house the electrolyte, plate, separator, and fittings. For example, a VRLA battery has positive and negative terminals and a vent device on its cover. The battery chute must be made of materials resistant to corrosion, vibration, and high/low temperatures.
In addition to the preceding features, the battery chute of a VRLA battery must have high strength to resist deformation and use a special structure. This is because the starved electrolyte structure of the VRLA battery requires that the battery be assembled in a tight manner, so as to facilitate full contact between the plate and the electrolyte. However, tight assembly brings relatively high pressure to the battery chute. Therefore, a larger battery capacity indicates a higher pressure borne by the battery chute.

## Slide 23: Container and Cover
The battery chute houses the electrolyte, battery plate, battery separator, and accessories. For example, there are the positive terminal, negative terminal, and exhaust unit in a VRLA battery. The battery chute must be made of corrosion-, vibration-, and high/low-temperature-resistant materials.

## Slide 24
Battery Overview
Lead-acid Battery
  Overview
  Battery Structure
  Working Principle
Lithium-ion Battery
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 25: Working Principles – Main Reaction
Double-sulphate theory
  This theory can be described as follows: When a lead-acid battery is discharged, the active substances at the positive and negative electrodes change to lead sulfate (PbSO4). After the battery is charged, the active substances return to the original state. That is, the active substances at the positive electrode change to lead dioxide (PbO2), and those at the negative electrode change to sponge lead (Pb).
The main reaction constitutes a chemical system of 2 V electromotive force for a single cell.
Main reaction: PbO2+2H2SO4+Pb 2PbSO4+2H2O
Positive electrode:
Negative electrode:
Discharging
Charging
Notes: After a battery is discharged, the new compound can be restored to the original active substance by injecting the external DC power with the appropriate reverse current. This process is called charging. The battery can be discharged again after this process.

## Slide 26: Working Principles – Side Reaction
Positive electrode:
Negative electrode:
At the end of charging and during overcharging, in addition to the reaction of active substances, the preceding two reactions occur at the positive and negative electrodes. At this time, PbSO4 is almost completely converted to PbO2 and Pb in charging state. The potential of the reaction increases. The side reactions including oxygen evolution reaction (OER) and hydrogen evolution reaction (HER) will dominate.
Therefore, overcharging may cause battery swelling due to the side reactions.
Notes: Negative electrode overcapacity design: Due to OER and HER, if the gas generated by the reaction cannot be reused, the battery will lose electrolyte and dry up. For the early traditional lead-acid battery, because of OER, HER, and H2 and O2 escape from the battery, the gas cannot be recombined, which is an important reason that acid and water need to be added frequently during maintenance. The VRLA battery can reuse O2 inside the battery and inhibit HER, overcoming the main drawbacks of the traditional lead-acid battery.
Oxygen recombination: At the end of charging and during overcharging, a side reaction occurs at the positive electrode and O2 is generated. Slight overpressure occurs near the positive electrode. This pressure pushes O2 to move to the negative electrode through the microporous gas channel between electrodes. O2 is combined with Pb at the negative electrode to produce PbO, which reacts with H2SO4 to produce PbSO4. During charging, PbSO4 is reduced to produce the active substance Pb. In this way, O2 produced by the positive electrode is absorbed. In actual use, there is always a small amount of gas that cannot be recombined. A one-way safety valve is installed on the battery cover so that redundant gas inside a battery can be exhausted to prevent the internal pressure of the battery from being too high. This is called valve regulation.
In lead-acid batteries, the negative electrode provides two functions. At the end of charging and during overcharging, on one hand, the sponge lead in the plate reacts with the O2 generated by the positive electrode and is oxidized into lead monoxide (oxygen recombination). On the other hand, PbSO4 in the plate will be reduced by electrons transmitted from the external circuit, and will be changed to sponge lead.

## Slide 27: Working Principle – Terminal Voltage Changes During Charging and Discharging
O
A
B
C
D
E
F
G
1.6
1.8
2.0
2.2
2.4
2.6
Time (T)
Voltage (V)
Notes: Charging: At the beginning, the terminal voltage increases dramatically along the OA section. When the voltage reaches point A, the terminal voltage rises slowly (ABC section). After the battery level reaches 90%, the side reaction (HER) at the negative electrode occurs. At this time, the terminal voltage of the battery reaches point D, and gas is emitted from the two electrodes.
Discharging: The terminal voltage decreases significantly along the OE section. Then, the discharge voltage slowly decreases with time (EFG section). As the discharge continues, the active substances at the positive and negative electrodes gradually change to PbSO4, which spreads to the depth. The formation of PbSO4 decreases the porosity of active substances, which increases the difficulty of H2SO4 spreading to the inside of the micropore, leads to poor conductivity of PbSO4, and increases the internal resistance of the battery. All these factors result in the sharp drop of the battery terminal voltage after the G point of the discharge curve, finally reaching the specified EOD voltage.

## Slide 28
Battery Overview
Lead-acid Battery
Lithium-ion Battery
  Overview
  Battery Structure
  Working Principle
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 29: Definition
Lithium-ion batteries are secondary batteries developed based on lithium batteries.
  The positive electrode material of lithium batteries is manganese dioxide or thionyl chloride, and the negative electrode material is metal lithium. After a battery is assembled, the battery has voltage and does not need to be charged.
  In the early 1990s, Sony invented batteries with carbon materials as the negative electrode and lithium compounds as the positive electrode. In the process of charging and discharging, lithium ions, instead of lithium, exist. These batteries are called lithium-ion batteries.
Notes: Primary cell: metal lithium battery and traditional dry cell.
Fuel cell: hydrogen fuel cell, which is used in automobiles and drones.
Dry cell: The positive electrode is a carbon rod, coated with a mixture of graphite and manganese dioxide. The negative electrode is zinc. The electrolyte is a mixture of ammonium chloride and starch, which generates electrical energy through the reaction of ammonium chloride and zinc.
Hydrogen fuel cell: Electrical energy is generated by the chemical reaction of hydrogen and oxygen. Chemical energy is directly converted into electrical energy. The safety and storage cost of hydrogen fuel still restrict the development of hydrogen fuel cells.

## Slide 30
Notes: Secondary cell:
Nickel-cadmium battery: Nickel-cadmium batteries are early rechargeable batteries used for shavers and other small electronic devices and cause heavy metal contamination.
Nickel-metal hydride battery: Nickel-metal hydride batteries cause slight contamination and are used to replace nickel-cadmium batteries. The batteries require precious metals as catalysts, and therefore are expensive.
Lead-acid battery: Large-sized lead-acid batteries are used for automobiles, communications, and UPSs, and cause heavy metal contamination. Lead-acid batteries are low-cost, average in performance, and mature in technology.
Lithium-ion battery: Medium- and large-sized lithium-ion batteries are used for consumer products such as mobile phones and laptops as well as automobiles, communications devices, electric tools, and drones.

## Slide 31: Classification
Lithium-ion batteries use positive electrode materials such as lithium cobalt oxide (LCO), lithium nickel oxide (LNO), lithium manganese oxide (LMO), lithium nickel manganese cobalt oxide (NCM)/lithium nickel cobalt aluminum oxide (NCA), and LFP.
Based on the electrolyte form, lithium-ion batteries are classified into liquified lithium-ion batteries and polymer lithium-ion batteries.
LFP batteries with liquid electrolytes are commonly used in data centers.
Positive electrode materials
LFP
NCM/NCA
LCO
LMO
LNO
Electrolyte
Liquid electrolyte
Liquified lithium-ion battery
Polymer lithium-ion battery
Polymer electrolyte
Notes: The electrolyte of liquified lithium-ion batteries is liquid, and the electrolyte of polymer lithium-ion batteries is a gel or solid polymer. From the appearance aspect, polymer lithium-ion batteries have a pouch with easy shaping while liquified lithium-ion batteries are cylindrical or prismatic.
Because the material production process is complex, the cost of polymer lithium-ion batteries is very high. Therefore, most lithium-ion batteries in the market are liquified lithium-ion batteries.
LFP and NCM/NCA batteries are mainly used in China. LFP batteries have rich raw materials, long service life, and good safety performance, and are used in energy storage systems. NCM/NCA batteries have high energy density and are mainly used in power vehicles.
LCO batteries are used in small digital devices as mobile phones and laptops. LMO materials are mainly used for small lithium batteries and power batteries. LNO materials have poor safety and are difficult to synthesize, and therefore are seldom used.
NCM and NCA batteries are the main trend in the future. Different combinations of three elements can enable the positive electrode materials to deliver different performances, meeting diversified application requirements.

## Slide 32
Battery Overview
Lead-acid Battery
Lithium-ion Battery
  Overview
  Battery Structure
  Working Principle
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 33: Internal Structure
Positive electrode: transition metal oxides (containing lithium) with a conductive agent and an adhesive, coated on an aluminum foil to form a positive plate
Negative electrode: formed by coating a laminated graphite with a conductive agent and an adhesive on a copper foil
Electrolyte: composed of electrolyte and organic solvent
Separator film: composed of a polyethylene (PE) or polypropylene (PP) microporous film. It isolates the positive and negative electrodes, preventing the passage of electrons while allowing that of lithium ions.
Shell: aluminum foil (pouch), steel shell, or aluminum shell.
Structure of a lithium-ion battery
Negative electrode tab
Positive electrode
Positive electrode tab
Separator film
Sealant
Negative
electrode
Aluminum-plastic bag
Notes: Why is aluminum foil used for the positive electrode and copper foil used for the negative electrode?
Causes:
1. Copper foil and aluminum foil feature good conductivity, good flexibility, and low price. Two processing methods are mainly used for lithium-ion batteries: winding and lamination. If winding is used, the electrode plate used for the battery must be flexible enough so that it is not broken during winding. Among metal materials, copper foil and aluminum foil are relatively flexible. In addition, considering the cost of preparing batteries, copper foil and aluminum foil are relatively cheap. Copper and aluminum resources are abundant around the world.
2. Copper foil and aluminum foil are relatively stable in the air.
3. The potentials of the positive and negative electrodes of the lithium-ion battery determine that aluminum foil is used for the positive electrode and copper foil is used for the negative electrode. The potential of the positive electrode is high, and the copper foil tends to be oxidized at a high potential. However, the oxidation potential of the aluminum foil is high, and there is a dense oxide film on the surface of the aluminum foil, which well protects the internal aluminum. Aluminum forms a lithium aluminum alloy when the negative electrode is at the ground potential, that is, aluminum is embedded with lithium when it is at the negative electrode. Similarly, copper is oxidized at the positive electrode due to the high potential. Therefore, the two types of metals are selected mainly because of their stability at different potentials.

## Slide 34
Notes: In commercial applications, lithium-ion batteries need to be assembled into packs. For consumer goods such as mobile phones, laptops, and electric tools, a battery pack contains a small number of batteries and is easy to assemble. In the energy storage and electric vehicle fields, a battery pack consists of thousands of batteries. These fields have high requirements for the battery structure and pack structure.
A complete battery pack includes the shell, electrochemical cell, sampling line, balance line, protection board, positioning device, heating board (optional), and heat dissipation device (optional).

## Slide 35: Positive Electrode Materials
Positive electrode material: Positive electrode materials include transition metal oxides or polyanionic compounds containing lithium and have a layered, spinel, or olivine structure. The materials provide a lithium source and have a stable lithium deintercalation capability, which determines the lower limit of safety of a lithium-ion battery.
Layered LiCoO2
Spinel LiMn2O4
Olivine LiFePO4
Positive Electrode Materials
LFP
LMO
LCO
NCM/NCA
LNO
Notes: Why positive electrode materials determine the lower limit of safety of a lithium-ion battery? When the temperature is excessively high, the positive electrode material tends to decompose. For example, LCO decomposes and generates a large amount of oxygen, but LFP is difficult to decompose.
LFP and NCM/NCA materials are mainly used in China, and LMO technology is not mature in China.
LFP does not contain expensive elements. The raw material is cheap and the resource is very rich. LFP batteries have moderate operating voltage (3.4 V), good plateau characteristics (extremely stable voltage), large theoretical capacity (170 mAh/g), and stable structure. They are compatible with most electrolyte systems and have good storage performance. LFP batteries are non-toxic and are real green materials.
The cycle life of LMO batteries ranges from 300 to 700 times.

## Slide 36: Negative Electrode Materials
Requirements for negative electrode materials:
  Electronic conductivity and ion conductivity are excellent.
  Intercalation and deintercalation reactions of lithium ions in carbon are fast.
  The existence of lithium ions in electrode materials is stable.
  A compact and stable solid electrolyte interphase (SEI) can be generated on the negative electrode surface to prevent the electrolyte from continuously reducing on the surface.
  In the charge and discharge cycle of the battery, the volume of the carbon material at the negative electrode changes slightly.
Common negative electrode material: graphite
Graphite molecular structure
Notes: Fast intercalation and deintercalation reactions of lithium ions in carbon: The diffusion coefficient of lithium ions in solid phase is large, and the moving impedance of lithium ions at the electrode/electrolyte interface is small. That is, the charge speed should be fast.
Slight volume change: Otherwise, the battery will bulge during charging and discharging.
Graphite structure: layered structure. Crystal specifications:
1. distance between adjacent graphite sheets (the value of ideal single-crystal graphites is 0.3354 nm). 2. thickness of a graphite sheet stacked in a direction perpendicular to it
Graphite intercalation mechanism: When lithium is completely embedded, the structure expands by about 10%.
Chemical activity: The activity increases with the charge state (lithium intercalation). The negative electrode is oxidized by air, and reacts violently and burns when contacting with water. Exercise caution when removing cells, especially fully charged cells.
Thermal stability: More active and worse thermal stability at higher temperatures

## Slide 37
Notes: SEI:
  Formed when the electrolyte is reduced when the battery is charged for the first time.
  Provides ion conduction and electronic insulation.
  Prevents graphite structure damage due to solvent intercalation.
  Ensures long-term and stable graphite cycles.
  Features stability, density, and low impedance.
Summary: During the first charge and discharge of a liquified lithium-ion battery, the electrode material and electrolyte react on the solid-liquid interface, forming a passivation layer that covers the surface of the electrode material. The passivation layer is an interphase layer that has features of the solid electrolyte. It is an electronic insulator but a good conductor of Li+. Li+ can be freely embedded and detached through the passivation layer. Therefore, the passivation layer is called the SEI.
The formation of the SEI film has a very important effect on the properties of electrode materials. On the one hand, the formation of the SEI film consumes some lithium ions, which increases the irreversible capacity of the initial charge and discharge and reduces the charge and discharge efficiency of the electrode material. On the other hand, the SEI film is insoluble in an organic solvent and can stably exist in an organic electrolyte solution. The SEI film does not allow a solvent molecule to pass through. This prevents the co-intercalation of the solvent molecule, therefore avoiding the damage to electrode materials caused by co-intercalation and greatly improving the cycle performance and service life of electrodes.

## Slide 38: Electrolyte
Electrolyte:
  Provides a medium for rapid conduction of lithium ions, and requires lithium ions (dissociating lithium salts).
  To dissolve the preceding lithium salt and additives, a solvent is required, which determines a lower limit of high and low temperature characteristics of batteries.
  To protect the reaction interface, a protective film (SEI) is formed on the (positive) negative electrode surface, and a film additive is required. The additive determines the interface of the material and the upper limit of the battery cycle.
Dissolving lithium salt to provide Li+ fluidity, with the cost accounting for about 30%
Providing lithium ions, with the cost accounting for about 60%
Functionality, with the cost accounting for about 10%
Electrolyte
Solvents
Conventional solvent
New solvent
Conventional
lithium salt
New lithium salt
Additives
Lithium salt
Chain carbonate ester
Cyclic carbonate ester
EC
DMC, DEC, EMC
Notes: Electrolyte features:
High conductivity and good solubility for lithium ions: maximizing the number of transported lithium ions
Good chemical stability: no reaction with other materials in the battery
Good thermal stability: no decomposition reaction in a wide temperature range
Wide electrochemical window: stable in the range of 0 V to 4.5 V (compared with Li/Li+)
Good compatibility with electrode materials: forming a dense, stable, and effective passivation film
Environmentally friendly, easy to prepare, and low-cost
Additives: negative electrode film-forming additives, positive electrode film-forming additives, overcharge additives, and flame retardant additives

## Slide 39: Separator Film
The separator film must meet the following requirements:
  Has direct contact with the positive and negative electrodes (high and low potentials) as well as the electrolyte, requiring electrochemical stability (against electrochemical and other corrosion).
  Provides physical barriers between positive and negative electrodes to prevent short circuits, featuring insulation (separating electrons) and strength against puncture. Allows lithium ions to pass through. Currently, a micro porous structure is used to absorb the electrolyte.
  Provides an automatic shutdown mechanism with low shutdown temperatures and high rupture temperatures, ensuring good protection performance.
  Determines the lower limit of the battery safety, does not provide active substances. A thinner separator film is better in terms of energy density.
  A thin separator film requires a ceramic coating for separation; to ensure that the positive and negative electrodes are adhered to each other, glue is required sometimes.
Notes: The separator film materials are PE, PP
The separator film provides electronic insulation, ensuring mechanical isolation between the positive and negative electrodes.
The separator film has certain pore size and porosity, ensuring low resistance and high conductivity for lithium ions to pass through.
The separator film is resistant to electrolyte corrosion, and has sufficient chemical and electrochemical stability.
The separator film has good infiltrating property for electrolyte and good wettability to absorb electrolyte.
The separator film should have sufficient mechanical properties, including puncture strength and tensile strength. During charging and discharging, lithium ions will precipitate and crystallize. The crystal will puncture the separator film, causing a short circuit inside the lithium-ion battery. Therefore, the separator film thickness should be as small as possible.
The separator film provides an automatic shutdown mechanism with low shutdown temperatures and high rupture temperatures, ensuring good protection performance. This is the key point and represents the lower limit of the battery safety.

## Slide 40
Notes: Core indicators of the separator film:
Thickness: A thicker separator film indicates higher strength and safety, but results in lower energy density of the electrochemical cell and larger internal resistance.
Porosity: mostly 30%–50%. Large porosity is beneficial to the wetting and retention of the electrolyte and improves the electrical performance, but undermines safety.
Air permeability: reflects the separator film quality or state of being permeable. Uneven permeability may lead to uneven distribution of electrode current density, causing lithium plating.
Micropore size and distribution: If the pore size is too small, lithium ions cannot pass through. If the pore size is too large, a micro short circuit may occur inside the electrochemical cell.
Wettability: The internal resistance, electrode interface, and cycle performance of the electrochemical cell are affected. Wettability is related to the micropore size and porosity of the separator film.
Thermal shrinkage: Excessive shrinkage causes a short circuit between the positive and negative electrodes. The shrinkage rate in both the horizontal and vertical directions must be less than 5%.
Mechanical strength: indicates the tensile strength. The separator film must be strong enough to avoid damage due to force during winding.
Puncture strength: The separator film prevents particles or foreign objects on the positive and negative electrodes, burrs on the electrode plate, and lithium dendrites from penetrating and causing short circuits of the electrochemical cell.

## Slide 41
Battery Overview
Lead-acid Battery
Lithium-ion Battery
  Overview
  Battery Structure
  Working Principle
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 42: Working Principle
Li+ intercalation and deintercalation repeatedly occur at the positive and negative electrodes.
During charging, Li+ is deintercalated from the positive electrode and intercalated into the negative electrode (obtaining electrons).
During discharging, Li+ is deintercalated from the negative electrode and intercalated into the positive electrode (obtaining electrons).
Use compounds that can be intercalated into lithium ions as the positive and negative electrodes, so that the flow of lithium ions changes from uncontrollable to controllable after guidance.
Positive electrode reaction:
Negative electrode reaction:
Battery reaction:
Charging
Discharging
Charging
Discharging
Charging
Discharging

## Slide 43: Working Principle
Electrolyte
Separator film
Negative electrode
Li+
Li+
Li+
Li+
Li+
Li+
Li+
Li+
Li+
Li+
Positive electrode
Charging
Discharging
Notes: Li+ intercalation and deintercalation repeatedly occur at the positive and negative electrodes.
During charging, Li+ is deintercalated from the positive electrode and intercalated into the negative electrode.
During discharging, Li+ is deintercalated from the negative electrode and intercalated into the positive electrode.

## Slide 44: Charging Management
The CC-CV two-stage charging method is used. In the CC charging stage, the 0.5C–1C charge current is used.
Restricted voltages in the CC charging stage are as follows:
  When LiFePO4 materials are used for the positive electrode, the maximum value is 3.650 V. If 16 lithium-ion batteries are cascaded, the maximum value is 3.650 V x 16 = 58.40 V.
  If the positive electrode material is not LiFePO4, the maximum value is 4.100 V. If 16 lithium-ion batteries are cascaded, the maximum value is 4.100 V x 14 = 57.40 V.
Charging termination conditions in the CV charging stage are as follows:
  At the end of the CC charging stage, when the battery voltage reaches the charge voltage limit, the CV charging mode is used. The charging stops until the charge current is less than or equal to 0.01C, and the entire charging process is complete.
Lithium-ion battery charge curve
Notes: CC: constant current
CV: constant voltage
Charging is divided into three stages. The first stage is the pre-charge stage. In this stage, the battery management system (BMS) identifies the current voltage of the battery (cell). If the voltage is less than 3 V, the battery is charged with a small current (generally one tenth of the constant current). When the voltage increases to more than 3 V, the CC charging is performed based on the charge current limit, which is generally less than 1C (the range is adjustable and varies with different manufacturers). When the voltage reaches 4.2 V, the CV charging is performed for a certain period of time. When the current is less than or equal to 0.01C, the charging stops.

## Slide 45: Balancing Problems
The most difficult problem of lithium-ion batteries is inconsistency. The causes of inconsistency are as follows:
  Internal causes: material or manufacturing difference, capacity, internal resistance, self-discharge and cyclic attenuation rate
  External causes: temperature, charge current, and discharge current
Solutions:
  Remove the first and last batteries.
  Perform balancing management.
  Form battery groups.
Notes: After batteries are used for a period of time, the electrochemical cell performance may be inconsistent due to differences in the material, manufacturing, internal resistance, attenuation rate, and temperature of the electrochemical cell.
The standards for evaluating electrochemical cell pairing include internal resistance difference, voltage difference, and plateau difference.
Cell plateau: During CC charging, the voltage changes as follows: rising, stable, and rising. The stable voltage stage in the middle is the voltage plateau.

## Slide 46: Balancing Management (1)
The voltages of batteries 1, 2, and 4 are high. The voltage of battery 3 is low. All switches are off. C1 and C2 are not charged.
The pulse changes from low level to high level.
Switch 1 is turned on, and loop 1 is connected.
Battery 1 charges C1, and battery 2 charges C2. The voltages of batteries 1 and 2 decrease, and the voltage of battery 1 recovers.
The pulse changes from high level to low level, and switch 1 is off.
CLKIN Low to Hi
① SWITCH ON
CLKIN Hi to Low
ALL SWITCH OFF
C1, C2 Charge or Discharge
1st CLOCK
･･･
･･･
Notes: Balancing management can be implemented in many ways, including resistance balancing, inductance balancing, and capacitance balancing. The ultimate goal is to achieve consistency. Capacitance balancing is used as an example here.
ALL Switch OFF: Switches 1, 2, and 3 are turned off.
CLKIN Low to Hi: The clock pulse changes from low level to high level.
C1, C2 Charge or Discharge: The charging or discharging of the capacitors C1 and C2 depends on the capacity of the capacitors and the capacity of the corresponding batteries.
CLKIN HI to Low: The clock pulse changes from high level to low level.

## Slide 47: Balancing Management (2)
The voltages of batteries 2 and 4 are high. The voltage of battery 3 is low. All switches are off. C1 and C2 are charged.
The pulse changes from low level to high level.
Switch 2 is turned on, and loop 2 is connected.
Battery 2 charges C1, and C2 charges battery 3. The voltage of battery 2 decreases and then returns to normal. The voltage of battery 3 increases.
The pulse changes from high level to low level, and switch 2 is off.
CLKIN Low to Hi
② SWITCH ON
CLKIN Hi to Low
ALL SWITCH OFF
C1, C2 Charge or Discharge
･･･
･･･
2nd CLOCK
Notes: ALL Switch OFF: Switches 1, 2, and 3 are turned off.
CLKIN Low to Hi: The clock pulse changes from low level to high level.
C1, C2 Charge or Discharge: The charging or discharging of the capacitors C1 and C2 depends on the capacity of the capacitors and the capacity of the corresponding batteries.
CLKIN HI to Low: The clock pulse changes from high level to low level.

## Slide 48: Balancing Management (3)
The voltage of battery 3 is low. The voltage of battery 4 is high. All switches are off. C1 and C2 are charged.
The pulse changes from low level to high level.
Switch 3 is turned on, and loop 3 is connected.
Battery 4 charges C2, and C1 charges battery 3. The voltage of battery 3 increases, and the voltage of battery 4 decreases to normal.
The pulse changes from high level to low level, and switch 3 is off.
CLKIN Low to Hi
③ SWITCH ON
ALL SWITCH OFF
CLKIN Hi to Low
C1, C2 Charge or Discharge
･･･
･･･
3rd CLOCK
Notes: ALL Switch OFF: Switches 1, 2, and 3 are turned off.
CLKIN Low to Hi: The clock pulse changes from low level to high level.
C1, C2 Charge or Discharge: The charging or discharging of the capacitors C1 and C2 depends on the capacity of the capacitors and the capacity of the corresponding batteries.
CLKIN HI to Low: The clock pulse changes from high level to low level.

## Slide 49: Balancing Management (4)
The voltage of all battery is normal. All switches are off. C1 and C2 are charged.
The pulse changes from low level to high level.
Reset.
All switches are off.
The pulse changes from high level to low level.
CLKIN Low to Hi
RESET ON
ALL SWITCH OFF
CLKIN Hi to Low
ALL SWITCH OFF
･･･
･･･
4th CLOCK
Notes: ALL Switch OFF: Switches 1, 2, and 3 are turned off.
CLKIN Low to Hi: The clock pulse changes from low level to high level.
RESET ON: reset
CLKIN HI to Low: The clock pulse changes from high level to low level.

## Slide 50
Battery Overview
Lead-acid Battery
Lithium-ion Battery
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 51: Cycle Life
Lithium-ion battery
  100% DOD: up to 3000 cycles; deep discharge: at least 3000 cycles.
  50% DOD: up to 6000 cycles; shallow discharge: at least 6000 cycles.
Lead-acid battery
  100% DOD: about 150 cycles; deep discharge: frequently replacing lead-acid batteries in case of poor grid power.
  50% DOD: about 600 cycles; shallow discharge: frequently replacing lead-acid batteries in case of poor grid power.
Notes: The cycle life is obtained from the battery white paper released by Huawei.
DOD: depth of discharge

## Slide 52: Float Charging Life
70% EOL float charge at 25°C for lithium-ion batteries: up to 15 years; no need to replace within the life cycle of 15 years if grid power is good.
70% EOL float charge at 25°C for lead-acid batteries: up to 7 years; need to replace every 3–7 years even if grid power is good; labor-intensive and high battery cost.
Float charging life of lithium-ion batteries (15 years)
Typical float charging life of 12 V lead-acid batteries (3–7 years)
Notes: EOL: end of life

## Slide 53: Discharge Characteristics at Different Rates
Short-time discharge at a high rate for lithium-ion batteries: More energy is discharged. As the discharge rate increases, the discharge capacity remains stable and can exceed 90%.
Short-time discharge at a high rate for lead-acid batteries: Less energy is discharged. As the discharge rate increases, the discharge capacity decreases rapidly. More batteries are required to offset the disadvantage, which increases the battery investment.
Comparison of discharge characteristics between lead-acid and lithium-ion batteries at different rates
Lithium-ion battery
Maintenance-free lead-acid battery (advanced)
Lead-acid battery (general type)
Discharge conditions
Discharge capacity (%)
Lithium-ion
battery
Lead-acid
battery
(general type)

## Slide 54: Footprint and Bearing Capacity
Weight/Energy density (Wh/kg) ratio: 3:1
  Lithium-ion battery: 100–150; lead-acid battery: 30–50
Volume/Energy density (Wh/L) ratio: 3:1
  Lithium-ion battery: 200–300; lead-acid battery: 60–90
Footprint and bearing capacity comparison between lead-acid batteries and lithium-ion batteries
Battery system specifications
200 kW, nominal voltage: 380 V, backup time: 30 min
Battery
Battery composition
Reduced building load-bearing capacity
Improved space utilization
Less capacity required
Lead-acid battery
Lithium-ion battery

## Slide 55: Storage Environment Requirements
For a data center that requires high availability, a small number of spare batteries are required for backup to shorten the maintenance preparation time. These batteries must be stored according to the requirements of the battery manufacturer.
Item | Lead-acid Battery | Lithium-ion Battery
Ambient temperature | 5–40°C (recommended temperature: 20–30°C) | 0–40°C (recommended temperature: 20–30°C)
Relative humidity | ≤ 95% | 
Others | The environment is dry, ventilated, and clean. Batteries must not contact with corrosive or organic solvents. Keep batteries away from direct sunlight and at least 2 meters away from heat sources. | 

## Slide 56: Operating Temperature
The operating temperature of common lithium-ion cells ranges from –20°C to +55°C. Therefore, no air conditioner is required.
  When the temperature is low, the dynamics deteriorates, and lithium plating tends to occur during charging. Generally, only discharging is performed.
  The oxidation-reduction reaction on the surface of the positive and negative electrode material is more intense at a higher temperature.
The operating temperature of lead-acid batteries ranges from 15°C to 25°C. Therefore, air conditioners are required.

## Slide 57: Safety Comparison
Our pursuit is to maximize stored and released energy and meet high energy density requirements within a safe and controllable range during the life cycle. With existing technology, a lithium-ion battery can be safe and controllable. From this perspective, a current lithium-ion battery is a relatively ideal battery product.
 | Lithium-ion battery | Lead-acid battery
Positive and negative electrodes | LFP, NCM, and graphite materials are combustible and flammable. | Pb and PbO2 are flame retardants.
Electrolyte | Non-aqueous organic solvent, flammable | Sulfuric acid solution, non-flammable
Barrier | Separator film, PP/PE, flammable | Grid, non-flammable
 | 10–20 μm thick, easy to be pierced by dust and crystal dendrites. Internal short-circuits are easily caused by heat shrinkage. | 3–5 mm thick, difficult to be pierced; no heat shrinkage
Combustion | Internal short circuit, combustion, and explosion | Shell combustion
Safety comparison between lithium-ion batteries and lead-acid batteries
Notes: LFP: lithium iron phosphate
NCM: ternary material

## Slide 58: Summary
Smaller size and lighter weight
(more than 3 times)
1
Longer cycle life
(more than 4 times)
2
Good discharge characteristics
3
Good environmental adaptability
4
Lead-acid battery
Lithium-ion battery
Environmental protection
5
Poor safety
6
Features of
lithium-ion
batteries
Notes: Lead-acid batteries contain lead, which is a heavy metal and harmful to the environment.

## Slide 59: Battery characteristics for Data Center
In recent years, with the rapid development of the Internet industry, many IT companies, such as Baidu, Alibaba, Tencent, Google, and Microsoft, are building more and more large data centers for the new network services. Geographical centralization and size expansion are the transformations facing data centers. High density and high reliability are the higher demands posed on storage battery.
High power density & excellent discharge performance
Small difference in capacity and voltage among battery
Simple battery installation and maintenance
Small footprint, saving space

## Slide 60
1.(Single)Based on the electrolyte content, storage battery can be classified into ( ).
A. Flooded lead-acid battery and Starved-electrolyte battery
B. AGM and GEL storage battery
C. Lead-acid and alkaline storage battery
D. Primary and secondary storage battery
2.(Single)Which of the following components is responsible for exhausting the excessive gas in the battery? ( )
A. Battery chute
B. Battery plate
C. Safety valve
D. Electrolyte
Notes: A
C

## Slide 61
(Short Answer Question)What does a lithium-ion battery consist of?
(Short Answer Question)What are the common positive electrode materials for lithium-ion batteries?
(Short Answer Question)What is the working principle of lithium-ion batteries?
Notes:   1. Positive electrode, negative electrode, electrolyte, separator film, and shell.
  2. Positive electrode materials: LFP, LMO, LCO, NCM/NCA, and LNO.
  3. Lithium ions can be intercalated into and deintercalated from the positive or negative electrode.

## Slide 62
Basic Knowledge of Batteries
Knowledge About Lead-acid Batteries
Knowledge About Lithium-ion Batteries
Comparison Between Lead-acid Batteries and Lithium-ion Batteries

## Slide 63
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 65
1.0
1.0
V5R2
V2R0
Guo Bian/WX337261
2017.03.29
New
HCIA-DCF
Wang Pulin/WX763618
2020.12
Li Shaofeng/l00486775
Update
2020.01.25
Update
2020.01.25
Update
2020.01.25
Update
2020.01.25
Update