## Slide 1: Air Conditioning System Introduction

## Slide 2
This chapter describes working principles of an air conditioning system, classification of air conditioning system, common air processing devices.

## Slide 3
On completion of this course, you will be able to:
  Understand working principles of air conditioning systems;
  Understand classification principles and types of air conditioning systems;
  Have general knowledge of some common air handling equipment;
  Understand basic knowledge of air conditioning air systems;
  Understand common air conditioner terms.

## Slide 4
Working Principles of Air Conditioning System
Classification of Air Conditioning System
Air Handling Equipment
Air Conditioning Air System
Common Air Conditioner Terms

## Slide 5: Development History of Air Conditioning Systems
In 1901, Dr. Willis Carrier established the world's first air-conditioning test lab in the United States.
In 1902, Dr. Carrier designed the world's first set of scientific air conditioning systems.
In 1922, Dr. Carrier invented the world's first centrifugal chiller.
In 1930, comfort air conditioners grew rapidly all over the world and applied to cinemas, theaters, and shopping malls.
In 1980, a computer room air conditioner (CRAC) cut a striking figure in China as a dedicated air conditioning model.
After 2002, data centers develop rapidly, further promoting the growth of CRACs.

## Slide 6: What is an Air Conditioner?
An air conditioner performs air conditioning;
The following indicators are designed for air: temperature, humidity, and cleanliness;
An air conditioner is designed to adjust the temperature, humidity, and cleanliness of air, with the goal of creating a comfort living and working environment.
Notes: For comfort air conditioners, ensure that the following indoor parameters that are designed for thermal comfort and health purposes meet requirements: temperature, humidity, fresh air volume, wind speed, noise level, and indoor air dust concentration. For data center air conditioners, there are no specific requirements for the fresh air volume, wind speed, and noise level, because data center air conditioners primarily serve devices. However, these three aspects need to be considered if someone is on duty in a data center.

## Slide 7: Refrigeration Principle (1)
Refrigeration process
  After absorbing the heat of substances to be cooled in an evaporator, a liquid refrigerant vaporizes and becomes low-pressure and low-temperature steam. After being absorbed and compressed by a compressor, the steam becomes high-pressure and high-temperature steam. Then, the steam enters a condenser and discharges heat to cooled substances, and is condensed into a high-pressure and medium-temperature liquid. After passing a throttling device, the liquid becomes the low-pressure and low-temperature liquid refrigerant. The liquid refrigerant then enters the evaporator. As such, cyclic refrigeration is realized.
Expansion valve
Evaporator
Condenser
Compressor
Notes: If being classified by refrigeration principles, many refrigeration methods are available, for example, steam compression refrigeration, lithium bromide absorption refrigeration, steam jet refrigeration, air expansion refrigeration, and electrochemical refrigeration. Air conditioners using artificial cold sources primarily use the steam compression refrigeration method and the lithium bromide absorption refrigeration method. Comfort and dedicated air conditioners primarily use the steam compression refrigeration method. The lithium bromide absorption refrigeration method is used only in areas without sufficient power supply. Therefore, only the steam compression refrigeration method is described in this slide.

## Slide 8: Refrigeration Principle (2)
Throttling (Pressure Releasing)
Compression
Vaporizing
Condensing
A compressor compresses the low-temperature and low-pressure saturated or superheated gas into a high-temperature and high-pressure superheated gas, for outdoor heat exchanging purposes.
The high-temperature and high-pressure superheated gas is condensed into a high-temperature and high-pressure saturated or supercooled liquid in a condenser.
A refrigerant vaporizes in an evaporator and becomes a low-temperature and low-pressure saturated or superheated gas, and then absorbs heat from indoor air.
After a throttle, the high-temperature, high-pressure liquid releases pressure. As a result, the refrigerant vaporizes. The high-temperature, high-pressure liquid also absorbs much heat to reduce the temperature of the liquid refrigerant. As a result, a low-temperature and low-pressure substance in both gas and liquid forms is formed.
Air Conditioner
Notes: Process 1: Compression process (adiabatic pressurizing) - This is an adiabatic compression process, involving only compression and not involving heat transfer. After low-temperature and low-pressure steam is compressed in a compressor, the steam pressure becomes greater. The outside world performs energy working for the steam in the form of mechanical energy. As a result, the steam obtains energy and its temperature rises. The compression aims to enable the refrigerant to release heat so that the steam temperature becomes higher than the outside temperature and the heat in the system can be released.
Process 2: Heat radiation process (equal-pressure heat radiation) - A condenser condenses the high-temperature and high-pressure steam that comes from the compressor, and releases the heat in the system to the outside world. Then, the temperature of the steam is reduced, but the pressure does not change. As a result, the steam changes to a liquid refrigerant. In summary, this process can be understood as reducing the temperature of the steam that is under normal atmospheric pressure, with the goal of changing the steam to a liquid.
Process 3: Throttling process - The normal-temperature and high-pressure liquid enters a throttle, which is actually a small hole that features dynamic adjustment. After passing the hole, the normal-temperature and high-pressure liquid enters a low-pressure and large-volume refrigerant pipe, forming the throttling effect. With the pressure being reduced, the liquid obtains a greater speed. As the pressure becomes too low, part of the liquid gasifies. As a result, the temperature of the liquid is reduced, and a low-temperature and low-pressure gas/liquid mixture is formed. The throttling aims to reduce the pressure of the refrigerant so that the boiling point of the refrigerant is lower than the indoor temperature and the refrigerant can absorb heat in a room and vaporize.

## Slide 9
Notes: Process 4: Heat absorption process (equal-pressure process) - The low-temperature and low-pressure gas/liquid mixture from the throttle enters an evaporator and absorbs the heat of the indoor air, so that the temperature of the indoor air decreases. As a result, the room is cooled. After the heat is absorbed, all liquid changes to a gas. The heat absorption is realized because the boiling point of the refrigerant is very low in the low pressure state. When the ambient temperature is higher than the boiling point of the refrigerant, the refrigerant absorbs heat continuously and changes to a gas.

## Slide 10: Refrigeration Principle (3)
Component | Refrigerant Status | Pressure Change | Temperature Change
Evaporator | Liquid – gas | Low pressure | Low temperature
Compressor | Gas – gas | Low pressure – high pressure | Low temperature – high temperature
Condenser | Gas – liquid | High pressure | High temperature – normal temperature
Expansion valve | Liquid – liquid/gas | High pressure – low pressure | Normal temperature – low temperature

## Slide 11: Introduction to the Four Major Components (1)
Four major components of a cooling system
  Compressor: Being the core of the refrigeration cycle, a compressor is the power device that enables a refrigerant to circulate in the cooling system. The compressor maintains low pressure for the refrigerant in an evaporator and high temperature and high pressure for the refrigerant in a condenser.
Scroll compressor
Screw compressor
Centrifugal compressor
Expansion chamber
Impeller
Notes: Refrigeration and air conditioning industries use the following five major types of compressors: reciprocal compressor, screw compressor, rotary compressor, vortex compressor, and centrifugal compressor. Reciprocal compressors are most widely used in small and medium commercial refrigeration systems. Screw compressors are mainly used in large commercial and industrial systems. Rotary compressors and vortex compressor are mainly used in household and small-capacity commercial air conditioning units. Centrifugal compressors are widely used in air conditioning systems of large-scale buildings.

## Slide 12: Introduction to the Four Major Components (2)
Four major components of a cooling system
  Condenser: Working with a condensing medium, a condenser condenses the saturated or superheated steam discharged by a compressor into a liquid;
  Evaporator: After passing a throttle, a liquid refrigerant enters an evaporator, absorbs heat, and vaporizes. As a result, the temperature of the substances to be cooled decreases, and refrigeration is realized.
Air-cooled condenser
Water-cooled condenser
Evaporator
Notes: If being classified by cooling media, condensers are available in water-cooled and air-cooled types. Water-cooled condensers use water as a cooling medium, with condensation heat being taken away by a temperature increase in water. Air-cooled condensers use air as a cooling medium, with condensation heat being taken away by a temperature increase in air.
If being classified by media to be cooled, evaporators are available in cooling air-type evaporators and cooling liquid-type evaporators.

## Slide 13: Introduction to the Four Major Components (3)
Four major components of a cooling system
  Throttling device: A throttling device performs throttling. Specifically, a throttling device regulates the circulation flow volume of a refrigerant. The throttling device regulates the flow of a high-pressure liquid refrigerant and reduces the pressure of the refrigerant so that the refrigerant can absorb heat and evaporate at the desired low pressure in an evaporator. In addition, the throttling device can automatically adjust the volume of the refrigerant that enters the evaporator based on the change in the heat load of the medium to be cooled.
Electronic expansion valve
Thermal expansion valve
Capillary tube
Notes: Expansion valves are available in two types, namely, thermal expansion valves and electronic expansion valves. A thermal expansion valve can control the amount of liquid to be supplied to an evaporator and throttle a saturated liquid refrigerant. When being classified by structure, thermal expansion valves are available in internal balance expansion valves and external balance expansion valves. Electronic expansion valves are mainly used in variable-frequency air conditioning systems. An electronic expansion valve adjusts the amount of liquid to be supplied to an evaporator based on a preset program. Electronic expansion valves adapt to the development of mechanical and electrical integrated refrigeration, feature excellent characteristics that thermal expansion valves do not have, and enable intelligent control for refrigeration systems.

## Slide 14
Working Principles of Air Conditioning System
Classification of Air Conditioning System
Air Handling Equipment
Air Conditioning Air System
Common Air Conditioner Terms

## Slide 15: Classification of Air Conditioners - By Application (1)
Air conditioners are classified into the following by application:
  Industrial air conditioner: Selected parameter values must meet requirements of the industrial process for air parameters;
  Comfort air conditioner: Selected parameter values must meet requirements for working conditions and rest conditions of people.

## Slide 16: Classification of Air Conditioners - By Application (2)
Air conditioners are classified into the following by application:
Adjustment Parameter Type of an Air Conditioner |  | Temperature | Humidity | Cleanliness | Airflow Speed | Operating Life
Industrial air conditioner | CRAC (precision) | Constant | Constant | Cleanliness required by data centers |  | Uninterruptible operation > 10 years
 | Clean air conditioner | Adjustable | Adjustable | Cleanliness required by industrial buildings |  | Intermittent operation ≤ 10 years
 | Medical air conditioner | Adjustable | Adjustable | Cleanliness required by the medical industry | < 0.25 m/s | Intermittent operation ≤ 10 years
Comfort air conditioner | Home air conditioner | Adjustable |  |  |  | Intermittent operation ≤ 10 years
 | Commercial air conditioner | Adjustable |  |  |  | Intermittent operation ≤ 10 years
 | Central air conditioner | Adjustable |  |  |  | Intermittent operation ≤ 15 years
Notes: There are many ways to classify air conditioning systems, for example, by the concentration degree of air conditioning devices, method of adjusting the system air volume, air speed in the system duct, and heat transfer principles.

## Slide 17: Classification of Air Conditioners - By Media (1)
Air conditioners are classified into the following by cooling system:
  Direct expansion air-cooled
  Direct expansion water-cooled
Air in a data center
Refrigerant
Outdoor air
Evaporator
Condenser
Indoor side
Outdoor side
Cooling tower/dry cooler
Cooling water/ethylene glycol
Outdoor air
Air in a data center
Evaporator
Condenser
Refrigerant
Indoor side
Outdoor side

## Slide 18: Classification of Air Conditioners - By Media (2)
Air conditioners are classified into the following by cooling system:
  Air-cooled chilled water
  Water-cooled chilled water
Cooling tower
Cooling water
Outdoor air
Air in a data center
Evaporator
Condenser
Refrigerant
Indoor side
Outdoor side
Chilled water
CW coil
Outdoor air
Chilled water
Evaporator
Condenser
Refrigerant
Indoor side
Outdoor side
Air in a data center
CW coil

## Slide 19: Classification of Air Conditioners - By Other Criteria
By the concentration degree of air conditioning devices
By the refrigeration architecture
By the method of adjusting the system air volume
Centralized air conditioning system
Semi-centralized air conditioning system
Distributed air conditioning system
In-room air conditioner
In-row air conditioner
In-cabinet air conditioner
Constant-air-volume air conditioning system
Variable-air-volume air conditioning system
Notes: Centralized air conditioning system: All air processing devices are installed in a central air conditioning room. Processed air is sent to the air conditioning system in each room using ducts. Centralized air conditioning systems apply to places with a large area, concentrated rooms, and basically the same ratio of the heat load to the humidity load in each room.
Semi-centralized air conditioning system: A semi-centralized air conditioning system consists of a centralized air conditioning system and end devices that process air. A semi-centralized air conditioning system is complex but achieves higher adjustment accuracy.
Decentralized air conditioning system: In a decentralized air conditioning system, air processing devices are installed in each room. Decentralized air conditioning systems apply to places with a small area, scattered rooms, and a large difference between the heat load and the humidity load.
Constant-air-volume air conditioning system: For an ordinary centralized air conditioning system, the volume of air supplied by fans is constant. The change in the load of an air conditioning zone is accommodated by changing the temperature of the supplied air. As such, the indoor temperature and humidity are adjusted.
Variable-air-volume air conditioning system: The temperature of supplied air is maintained at a certain degree by changing the volume of the supplied air. As such, the change in the load of an air conditioning zone is accommodated, and desired indoor temperature and humidity are obtained.

## Slide 20
Working Principles of Air Conditioning System
Classification of Air Conditioning System
Air Handling Equipment
Air Conditioning Ventilation System
Common Air Conditioner Terms

## Slide 21: Classification of Devices That Process Air Heat and Humidity
Direct-contact processing device
  The medium that exchanges heat and humidity with air is in direct contact with air. Specifically, a direct-contact processing device lets air flow on the surface of the medium or sprays the medium into air. Common direct-contact processing devices include water chambers and humidifiers.
Indirect-contact processing device
  The medium that exchanges heat and humidity with air is not in direct contact with air. The exchange of heat and humidity between the air and the medium is carried out using the metal surface of the device. Common indirect-contact processing devices include surface coolers, air heaters, evaporators, and condensers.
Direct contact (humidifier)
Indirect contact (surface heat exchanger)
Notes: After air flows into a water chamber, the nozzle sprays a lot of mist water droplets into the air. After the air comes into contact with the water droplets, they exchange heat and humidity. As such, the required temperature and humidity are obtained. A water chamber realizes a variety of air processing processes, but consumes a large amount of water, occupies a large area, and uses a complex water system. In addition, the water is easy to be polluted. This is why water chambers are not widely used in comfort air conditioners.

## Slide 22: Surface Heat Exchanger
Surface heat exchangers include air heaters and air coolers.
Light pipe air heater
Finned tube air heater
Electric heater
Finned tube air cooler
Finned tube air cooler
Notes: Surface heat exchangers include air heaters and air coolers. A surface heat exchanger enables a heat medium or a refrigerant to flow in the cavity of a metal pipe and the air to be processed to flow on the outer wall of the metal pipe. As such, heat is exchanged, and the purpose of heating or cooling air is realized. Radiators widely used in northern China belong to this type of heat exchangers.

## Slide 23: Humidifier (1)
Wet film humidifier
  When water in the tank is conveyed to the sprinkler on the top of a humidifier, the sprinkler sprinkles the top part of the wet film with water evenly. The water permeates through all layers in the wet film and is absorbed by the wet film. Then an even water film is formed. When dry air passes through the wet film, the dry air has a large area of contact with the wet film surface so that a large amount of water evaporates. A lot of water molecules are blown with air into the space that requires humidification to increase its air humidity.
Notes: Huawei precision air conditioners use wet film humidifiers.

## Slide 24: Humidifying Devices (2)
Electrode humidifier
  The electrodes of an electrode humidifier form a loop with water in a humidifier cylinder. The electrode humidifier heats the water until the water boils and generates steam. The amount of moisture generated by a humidifier is controlled by adjusting the level of water in the humidifier cylinder in use. The electrode humidifier is safe and reliable. It does not work without water. It controls precision through output power and is free from the impact of scaling. The electrode humidifier features large humidification amount and low acquisition cost. Electrode humidifiers are generally used in in-row precision air conditioners.
Electrode humidifier
Infrared humidifier
  An infrared humidifier uses extreme infrared rays to make water vibrate, so that the water obtains heat and then evaporates. An electrode humidifier has high requirements for the water quality, because scale generated in the humidifier cylinder may block the solenoid valve and affect the humidification efficiency. An infrared humidifier does not have this weakness. In addition, an infrared humidifier saves energy. Infrared humidifiers are generally used in in-room precision air conditioners.
Infrared humidifier
Notes: There are many ways to humidify air, for example, using a water chamber, dry steam humidifier, electric humidifier, electrode humidifier, infrared humidifier, ultrasonic humidifier, centrifugal humidifier, high-pressure spray humidifier, or wet film humidifier. In this slide, only electrode humidifiers and infrared humidifiers are introduced.

## Slide 25: Humidifying Devices (3)
Other humidifiers
High-pressure micro-mist humidifier
Dry steam humidifier
Notes: Working principles of a high-pressure micro-mist humidifier: A high-pressure micro-mist humidifier increases pressure on water to 7 Mpa using a high-pressure piston pump, and then sends the pressurized water to a dedicated nozzle using a high-pressure transmission pipeline. The nozzle atomizes the water to generate particles in 3 to 15 µm. The particles quickly absorb heat from the air and then vaporize and diffuse around. As such, the air is humidified and cooled. A high-pressure micro-mist humidifier can reach the humidification efficiency of 166 kg/kWh, which is more than 100 times that of an electrode or infrared humidifier.
Working principles of a wet film humidifier: A wet film humidifier sprinkles a water-absorbing filler with water. When the air to be processed flows through the filler, the water absorbs the sensible heat of the air and evaporates into steam. The steam enters the air. As a result, the air is humidified and its temperature is reduced.

## Slide 26: Dehumidifying Devices
Rotary dehumidifier
Refrigeration dehumidifier
Dry air outlet
Wet air inlet
Regeneration heater
Regeneration air inlet
Fixed splitter plate
Regeneration air outlet
Hygroscopic wheel
Notes: Refrigeration dehumidifiers are usually called dehumidifiers. When coming into contact with the cooling copper fins of a refrigeration dehumidifier, water vapor changes into water droplets. In the entire liquefaction process, the dehumidifier works as a device that converts gaseous water into liquid water.

## Slide 27
Working Principles of Air Conditioning System
Classification of Air Conditioning System
Air Handling Equipment
Air Conditioning Air System
Common Air Conditioner Terms

## Slide 28: Functions of Air System
Functions of air system: An air system properly organizes the flowing of indoor air, with the goal of ensuring that the temperature, humidity, speed, and cleanliness of the air in indoor work areas better meet requirements of the production process and human body comfort. The air system of an air conditioning system primarily consists of fans, ducts, air vents, and air valves.
Room
Room
Fan
Fan
Filter
Fresh air
exhausted air
Air valve
Return air
Supply air
Notes: Return air: After mixing with fresh air, a part of indoor air passes an evaporator again for temperature reducing. This part of indoor air is called return air.

## Slide 29: Airflow Forms (1)
Supplying air from the top of room (up supply) and returning air from the bottom of room (down return).
  Air supply vents are located at the top of an air-conditioned room, and air return vents are located at the bottom of the room. The airflow enters the room from the top and leaves the room from the bottom.
  This airflow form applies to industrial air conditioners that require a constant temperature and cleanliness, and also applies to comfort air conditioners that primarily supply hot air and are installed in rooms with a large floor height.
Airflow organization forms of up supply and down return
Notes: Airflow organization: Plan air supply vents and air return vents properly for an air-conditioned room, so that after being sent to the room through the air supply vents, air that is purified and undergoes heat and humidity processing can evenly eliminate the excess heat and excess humidity in the room when diffusing and mixing with air in the room. As such, the work area obtains uniform and stable temperature, humidity, airflow speed, and cleanliness, and requirements of the production process and human body comfortableness are met.
Strengths of up supply and down return: (1) Before entering the work area, the supplied air has sufficiently mixed with the air in the room, facilitating the formation of a uniform and stable temperature field, humidity field, and velocity field. (2) When both air supply vents and air return vents are located on sides, the air supply path is very long. To address the issue, ensure that the difference between the temperature of the supplied air and the temperature of the air in the room is large and that the volume of the supplied air is small.
Weaknesses of up supply and down return: (1) If air return vents need to be connected to air ducts, installing air ducts is difficult. (2) If centralized air return vents are used, noise in the data center has a significant impact.

## Slide 30: Airflow Forms (2)
Supplying and returning air both from the top of room (up supply and up return).
  When both air supply/return ducts and air supply/return vents are located at the top of an air-conditioned room, the airflow enters the room from the top and leaves the room also from the top.
  This airflow organization form applies to comfort air conditioners that are primarily used to reduce temperature and are installed in rooms with a small floor height, and also applies to rooms where air return vents cannot be provided at the bottom.
Airflow organization forms of up supply and up return
Notes: Strengths of up supply and up return: (1) Air supply/return ducts being installed at the top of a room or hidden in a ceiling do not take up the usage area of the room and easily match the interior decoration. (2) When air return ducts are installed at the top of a room, the return airflow can take away part of heat radiated by lighting devices in the ceiling, reducing the cold load in the work area in summer.
Weaknesses of up supply and up return: (1) As part of the work area is in the air supply area and part of the work area is in the air return area, it is difficult to form a uniform temperature field, humidity field, and velocity field. (2) If air vents are not properly planned, the air supply/return flow may be blocked, affecting the air conditioning quality.

## Slide 31: Airflow Forms (3)
Supplying air from the middle of side walls of room (central supply).
  Air supply vents are located in the middle of side walls of an air-conditioned room, and air return vents are located at the bottom of the room. The airflow enters the room from the middle of side walls and leaves the room from the bottom.
  For some tall air-conditioned rooms, if the actual work areas are in the lower parts of the rooms, you do not need to control the entire space, and you only need to control the lower parts of the rooms.
Airflow organization forms of central supply

## Slide 32: Airflow Forms (4)
Supplying air from the bottom of room and returning air from the top of room (down supply and up return).
  Air supply vents are located at the bottom of an air-conditioned room, and air return vents are located at the top of the room. The airflow enters the room from the bottom and leaves the room from the top.
  This airflow organization form applies to industrial air conditioners that need to take away a large amount of excess heat in the lower part of an air-conditioned room, and also applies to comfort air conditioners that are installed in crowded public buildings with a large floor height, for example, a theater.
Airflow organization forms of down supply and up return

## Slide 33: Introduction to Air Vents (1)
Louver
  Louvers are the most widely used air vents in air conditioning projects. Louvers can be installed on walls of air-conditioned rooms or sides of exposed ducts. Besides, louvers can be installed on ceilings of air-conditioned rooms or bottoms of exposed ducts.
  Common louver types: single-layer louver and double-layer louver.
Single-layer louver
Double-layer louver

## Slide 34: Introduction to Air Vents (2)
Air Diffuser
  Air diffuser is usually installed on the ceiling of an air-conditioned room or the bottom of an exposed. Air diffuser has a nice shape, easily matches the room decoration, and is one of the most widely used air supply vents.
  Common types: down air supply type and horizontal air supply type.
Round diffuser
Square diffuser
Notes: After being blown from a down-type diffuser, an airflow directly diffuses into the air-conditioned area, forming a steady, downward, direct airflow. Down-type diffusers are primarily used in scenarios in which the room clearance is very large (3.5 m to 4.0 m).
After being blown from a flat-type diffuser, an airflow diffuses around radially along the flat top, so that the supplied air is fully mixed with the indoor air before entering the air-conditioned area, with the goal of obtaining a relatively uniform temperature field and velocity field. Plat-type diffusers generally apply to industrial air conditioners that have requirements for the room-temperature fluctuation range and are installed in rooms with a small floor height, and also apply to comfort air conditioners that are installed in general public buildings.

## Slide 35: Introduction to Air Vents (3)
Vented floor
  Vented floor is generally installed on raised floors in data centers and used as downward air supply vents.
  Common types: mechanical type and electric type.
Mechanical vented floor
Electric vented floor
Notes: Variable-air-volume vented floor panels are available in two types: one type using adjustable air dampers (using physical blocks between openings), and the other type using both dedicated vented floor panels and adjustable fans. A vented floor panel can be mechanically or electrically controlled, but the price of the electrically controlled type is 10 times or even higher the price of the mechanically controlled type. A mechanically adjusted vented floor panel cannot increase the volume of vented air. In addition, it is difficult to control the adjustment accuracy. That is, the allocation of air in a data center almost cannot be adjusted. An electrically adjusted vented floor panel (adjusted by a fan) is not affected by the floor opening rate. The volume of supplied air is dynamically adjusted based on the rotating speed of the fan. Therefore, electrically adjusted vented floor panels can be used in scenarios in which a large amount of air is required or in data centers that have local hot spots. However, an electrically adjusted vented floor panel is less reliable and more expensive than a mechanically adjusted vented floor panel. The problem of local hot spots can be resolved using other methods, for example, increasing the number of horizontal flow air conditioners. Therefore, electrically adjusted vented floor panels are seldom used.

## Slide 36: Introduction to Air Vents (4)
Other air vents
Swirl vent
Striped vent
Lamp air supply diffuser
Nozzle

## Slide 37
Working Principles of Air Conditioning System
Classification of Air Conditioning System
Air Handling Equipment
Air Conditioning Air System
Common Air Conditioner Terms

## Slide 38: Cooling Capacity, EER and COP
Cooling capacity:
  Heat absorbed by the refrigerant on the low-pressure side in the evaporator in unit time when the air conditioner is refrigerating or the sum of heat removed from the enclosed space, room or area in unit time. The common unit is W or kcal/h.
  1 cal is the energy needed for making the temperature of 1g water rise by one Celsius degree. In international unit, energy is expressed by using joule. 1 cal = 4.184 J.
  Refrigeration ton: Refrigeration ton indicates the cooling capacity needed for freezing 1 ton of 0℃ saturated water into 0℃ ice within 24 hours；
    1 US refrigeration ton =3024 kcal/h = 3.517 KW.
Consumed power:
  Consumed power for refrigeration: total power consumed when an air conditioner is refrigerating(unit: W).
  Consumed power for heating: total power consumed when an air conditioner is heating (unit: W), including power consumed by the electric heater supplementing the heat pump.
Energy efficiency ratio (EER):
  Ratio of cooling capacity to input power under rated and specified conditions when an air conditioner is refrigerating. The value is expressed by using W/W.

## Slide 39: Refrigerant and Circulated Air Volume
Refrigerant:
  Refrigerant is also called refrigerating medium. It is an operating substance that circulates continuously in the refrigerating system by changing its state to realize refrigeration. Refrigerant absorbs heat of cooled medium (water or air) in the evaporator and evaporates and then transfers heat to surrounding air or water in the condenser and condenses;
  Common refrigerant: R22 (HCFC-22), R407C (HCFC-32/123/134a), and R410A (HCFC-32/123). R22 will create a greenhouse effect and damage the ozone layer and R407C and R410a will create a greenhouse effect;
  Types of refrigerant oil: R22, R407C, and R410A.
Circulated air volume:
  Air volume sent to the enclosed space, room or area under rated refrigerating conditions. Unit: m3/h;
  In a room, the air velocity has a great effect on human comfortableness. The air velocity in ordinary working areas is 0.4 m/s.

## Slide 40: Sensible Heat Ratio
Sensible heat ratio = sensible heat/total heat = sensible heat/(sensible heat + latent heat)
  Sensible heat refers to heat that can be sensed. It can cause temperature change of a substance but does not change the state of the substance;
  Latent heat changes the state of a substance but does not change the temperature when heat is absorbed or released;
    Latent heat of fusion refers to the heat absorbed or released when a substance changes from solid state to liquid state or from liquid state to solid state;
    Latent heat of vaporization refers to the heat needed when a substance changes from liquid state to gas state;
    Latent heat of liquid refers to the heat released when a substance changes from gas state to liquid state.
Example of latent heat: 335 J of energy is absorbed when 0ºC ice melts into 0ºC water.
Example of sensible heat: 4.186 J of energy is absorbed when 0ºC water is heated and becomes 1ºC water.

## Slide 41: Temperature
Temperature:
  Dry bulb temperature: temperature measured by using the thermometer not wrapped with wet gauze, as shown in the figure on the left.
  Wet bulb temperature: temperature measured by using the thermometer wrapped with wet gauze, as shown in the figure on the right.
  In general, the air is unsaturated and can absorb moisture. In this case, water on the wet gauze absorbs heat and evaporates. Therefore, the wet bulb temperature is generally lower than the dry bulb temperature. The lower the relative humidity of air is, the more water on wet gauze will evaporate. In this case, the wet bulb temperature is much lower than the dry bulb temperature. When the air is saturated, the two are the same.
Centigrade temperature (ºC):
  Under 1 atmospheric pressure, the freezing point of water is 0ºC and the boiling point is 100ºC.
Fahrenheit temperature (ºF): ºF=ºCx1.8+32; ºC=(ºF - 32)x5/9
Absolute temperature (K): K=273+ºC
Notes: The absolute temperature is the thermodynamic temperature, also known as Kelvin, It is one of the important parameters in thermodynamics and statistical physics.

## Slide 42: Humidity
Humidity: amount of steam in the air
  The most suitable humidity is 40% to 55% in the computer room.
  Too low humidity will easily generate static electricity; too high humidity will easily generate condensate water and cause short circuit of electric equipment.
Humidity | Definition | Meaning
Relative Humidity | Ratio of the actual amount of steam in the air to the maximum amount of steam that can be accommodated in the air under the same temperature and same pressure. It is expressed by using %. | Drying degree of air. The smaller the percentage is, the drier the air is.
Moisture content | Amount of steam in each kilogram of air (g) | Water volume in unit mass of air
Notes: Relative humidity: the ratio of the partial pressure of water vapor in wet air to the partial pressure of water vapor in saturated wet air with the same temperature and the same total pressure.

## Slide 43: Dew Point
Dew point: temperature when the air becomes saturated.
    Under certain atmospheric pressure and steam content, when the air becomes saturated and continuous cooling will form dew, the temperature at this time is dew point.
    In the air conditioning system, when the surface temperature of the evaporator or surface cooler is lower than the dew point of the air, steam in the air will condense, so as to achieve the objective of dehumidification.
    In a general computer room (24ºC, 50%), the dew point is 13.2ºC. Below this temperature, the surface of objects will form dew.
    The table below lists dew points in common computer room environments.
Dry Bulb Temperature (ºC) | Relative Humidity | Dew Point (ºC)
24 | 50% | 13.2
24 | 45% | 13.1
24 | 55% | 14.6
23 | 50% | 12.4
23 | 45% | 10.6
23 | 55% | 13.7
22 | 50% | 11.3
22 | 45% | 11.1
22 | 55% | 12.7

## Slide 44: Cleanliness
Cleanliness: content of dust (including microbes) in clean air.
  Code for Design of Data Centers raises the following requirement for dust concentration in computer rooms: under static or dynamic conditions, the number of dust particles greater than or equal to 0.5um is smaller than 17,600,000 in each cubic meter of air.
  When the air conditioning system in the computer room adopts a cycle generating unit, a primary efficiency or medium efficiency filter should be equipped. A fresh air system should be equipped with a primary efficiency or medium efficiency filter and a sub-high efficiency filter is preferred.
  Comparison table of filter levels:
Filter efficiency compare table about China USA and Europe |  |  |  |  |  |  |  |  |  | 
China GB/T14295 | Roughing |  |  |  | Medium efficiency |  |  | High efficiency |  | 
USA ASHRAE | C1 | C2,3,4 | L5 L6 | L7 | L8 | M9 M10 | M11 | M12 | M13 | M14
Europe CEN | G1 | G2 | G3 | G4 |  | F5 | F6 |  | F7 | F8
Europe EUROVENT | EU1 | EU2 | EU3 | EU4 |  | EU5 | EU6 |  | EU7 | EU8

## Slide 45
(Single)Which of the following devices is a direct-contact processing device?
  Humidifier
  Evaporator
  Electric heater
  Condenser
(Short Answer Question)What categories can air conditioning systems be classified into by media?
Notes: Answer of the first question: A.
Air-cooled cold air, air-cooled cold water, water-cooled cold air, and water-cooled cold water.

## Slide 46
Working Principles of Air Conditioning System
Classification of Air Conditioning System
Air Handling Equipment
Air Conditioning Air System
Common Air Conditioner Terms

## Slide 47
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 49
Shenjutao/WX352174
2017.07.11
New
HCIA-DCF
WangCong/wx760444
2020.04
Li Shaofeng/l00486775
Notes: 2015.7.4
  调整版权和页码对齐，位于参考线8.5到8.9之间。
2015.7.14
  新增更多信息和推荐的样例。
2015.8.3
  胶片主体和备注页，段落设置为“允许标点溢出边界”。
2015.8.4
  删除缩略语页。
2015.9.2
  新增备注页页眉，居于备注页正上方，显示本章标题。
2015.9.14
  删除“谢谢”那页的白色“谢谢”。
2017.11.8
  调整母版中标题宽度。