## Slide 1: Basic Knowledge of Precision Air Conditioners in Data Centers

## Slide 2
The slides describe the basic knowledge of precision air conditioners in data centers, as well as the technical principles and main components of the air-cooled precision air conditioner, chilled water precision air conditioner, and indirect evaporative cooling system.

## Slide 3
On completion of this course, you will be able to:
  Understand the features of data center air conditioners and the differences between data center air conditioners and household air conditioners;
  Understand the basic principles and main components of the air-cooled precision air conditioner;
  Understand the basic principles and main components of the chilled water precision air conditioner;
  Understand the basic principles and main components of the indirect evaporative cooling system;
  Understand the product architecture of Huawei precision air conditioners.

## Slide 4
Overview of Data Center Air Conditioners
  Functions and Application Scenarios
  Classification
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 5: Why Do We Use Air Conditioners?
If there are no specialized air conditioners for the computer room:
  Unable to maintain constant temperature - greatly reduce service life of electronic components.
  Partial superheat - sudden shutdown of equipment.
  Too high humidity in computer room - generate condensate water.
  Too low humidity in computer room - generate damaging static electricity.
  Not clean enough - main equipment damage and communication data error.
ANSI/TIA-942-2-2010 " Telecommunications Infrastructure Standard for Data Centers "
Space | Environmental requirements
Computer rooms, entrance rooms, access provider spaces, and service providers spaces in data centers | Temperature: 18 – 27ºC (64 – 81ºF ) dry bulb high altitude: reduce maximum dry-bulb temperature 1ºC for every 300m (1.8ºF for every 1000 ft) above 1800 m (5900 ft) altitude Maximum Relative Humidity (RH): 60% Maximum dew point: 15 ºC (59 ºF ) Minimum dew point (lower moisture limit): 5.5 ºC (42ºF ) ¹ Maximum rate of temperature change: 5 ºC (9 ºF ) per hour
Notes: 1. Dewpoint of 5.5 ºC - corresponds to approximately 44% RH at 18 ºC (64 ºF ) and 25% RH at 27 ºC (81 ºF ). | 
Notes: According to Arrhenius equation, electronic components degrade by 50% in terms of reliability for rise of temperature by each 10ºC.
On November 11, 2012, taobao.com encountered short shutdown due to superheat of computer room.
On the first day of transport during the Spring Festival period in 2013, the online ticketing website 12306.cn encountered shutdown due to superheat of computer room.

## Slide 6: Why Do We Use Precision Air Conditioner?
Data center air conditioner
  Used in data centers to cool IT equipment.
Advantages:
  High energy efficiency: COP>3.0
  High sensible heat ratio: > 0.9
  High air volume
  Cooling throughout the year
  High precision control over temperature and humidity
  Long service life: > 10 years
Notes: Coefficient of performance. Consumed power for refrigeration: total power consumed when an air conditioner is refrigerating (unit: W).Consumed power for heating: total power consumed when an air conditioner is heating (unit: W), including power consumed by the electric heater supplementing the heat pump.
Sensible heat ratio = sensible heat/total heat = sensible heat/(sensible heat + latent heat).

## Slide 7: Application Scenarios
Application
scenario
Modular data center
Container data center
Medium or large data center
Notes: In row air conditioner used in modular and container data center. In room air conditioner normally use in room air conditioner.

## Slide 8
Overview of Data Center Air Conditioners
  Functions and Application Scenarios
  Classification
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 9: Classification (1)
The mainstream cooling modes for data centers include mechanical cooling and free cooling.
  Mechanical cooling is implemented by the compressor operation of a cooling device. Direct expansion and water-cooled air conditioners are mainly used for mechanical cooling.
  Free cooling is implemented by free cooling sources to cool data centers. Direct fresh air cooling and indirect evaporative cooling are two major modes.
With the development of technology and energy-saving requirements, many new cooling methods are emerging, such as refrigerant pump cooling, fan wall cooling, heat pipe air conditioning, and liquid cooling.
This course mainly describes air-cooled precision air conditioners, chilled water precision air conditioners, and indirect evaporative cooling air conditioners that are widely used in data centers, and briefly introduces other technologies such as refrigerant pumps.
Notes: In different scenarios, data center air conditioners are classified in different ways. This course describes several common classification methods.

## Slide 10: Classification (2)
Classified by indoor unit layout
In-row air conditioner
In-cabinet air conditioner
In-room air conditioner
Notes: This section mainly describes the preceding three mainstream types. In addition, air conditioners are classified into the following types based on the indoor unit layout mode: backplane heat pipe air conditioner, top-mounted air conditioner, and bottom-mounted air conditioner.
To solve the problem of mixing of cold and hot air in the data center, in-room, in-row, and in-cabinet cooling modes are mainly used during data center design. In these modes, the air-conditioning system is integrated with a room, a cabinet row, or a single cabinet to reduce air mixing. This improves predictability, density, and efficiency, and also brings many other benefits. The preceding figure shows the differences between in-room air conditioners, in-row air conditioners, and in-cabinet air conditioners.

## Slide 11: Classification (3)
Classified by cooling mode
Air-cooled air conditioner
Chilled water air conditioner
CRAC
20°C
Cold air
Free cooling air conditioner
Notes: Air conditioners are classified into air conditioners with dual cooling sources and other types of air conditioners. This section mainly describes air-cooled air conditioners, chilled water air conditioners, and free cooling air conditioners.

## Slide 12: Classification (4)
Classified by airflow organization
Upflow air conditioner
Downflow air conditioner
Air conditioner with horizontal airflow
External thermal insulation material
Air duct
Device
Device
Device
Front
Air conditioner
Notes: Upflow air conditioners can be equipped with the tuyere or air duct for overhead air supply. Air supply with a tuyere applies to small- and medium-sized equipment rooms where the air supply distance of a single air conditioner is less than 15 m and the power of a single cabinet is less than 2 kW. Air supply with an air duct applies to equipment rooms with long air supply distances and low power.
For downflow air conditioners, the raised floor must be at least 400 mm above the ground. Thermal insulation measures must be taken for the floor. This mode applies to scenarios where the air supply distance of a single air conditioner is less than 15 m. Aisle containment can improve efficiency.
In-row air conditioners with horizontal airflow apply to high-power equipment rooms and do not require raised floors.

## Slide 13
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
  Basic Principles
  Components
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 14: Basic Principles (1)
1——2: The low-temperature and low-pressure vapor is compressed into high-temperature and high-pressure vapor by the compressor.
2——3: The heat of the high-temperature and high-pressure vapor is released by the condenser to form medium-temperature and high-pressure liquid.
3——4: The saturated liquid passes through the expansion valve to form a low-temperature and low-pressure gas-liquid mixture.
4——1: The gas-liquid mixture absorbs heat through the evaporator to form low-temperature and low-pressure vapor.
1
2
3
4
Condenser
Evaporator
Expansion
valve
Compressor

## Slide 15: Basic Principles (2)
Direct expansion air-cooled
  Device refrigerant: refrigerants such as R410A, R407c, and R22;
  Application scenarios: small and medium-sized data centers without 24 h chilled water source (with the cooling capacity less than 500 kW);
  Characteristics:
    Simple structure, easy and quick installation, and low cost;
    Relatively small, independent refrigeration cycle, and easy maintenance;
    Suitable for areas where water is scarce and where a cooling water system is absent;
    Relatively low cooling energy efficiency ratio;
    Not supporting long-distance installation. (Because such installation results in heavy cooling loss).

## Slide 16: Basic Principles (3)
Direct expansion water-cooled
  Device refrigerant: refrigerants such as R410A, R407c, and R22;
  Application scenarios: areas with abundant water sources;
  Characteristics:
    Convenient and quick installation; (because refrigerants have been filled in factories);
    Supporting long-distance installation;
    A mixed solution of water and ethylene glycol generally required;
    More suitable for large-scale systems with a cooling tower.
Compressor
Evaporator
Plate heat exchanger
Throttling device
Indoor unit
Dry cooler
Cooling tower
Water
Cold air
Hot air
Evaporator
Throttling device
Compressor
Plate heat exchanger

## Slide 17
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
  Basic Principles
  Components
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 18: Components of a Huawei Air-Cooled Air Conditioner
No. | Name
1 | Compressor
2 | Discharge temperature sensor
3 | High pressure switch
4 | High pressure sensor
5 | Oil separator
6 | One-way valve
7 | Exhaust pipe needle valve
8 | Oil trap
9 | Outdoor unit
10 | Inverted U-shaped trap
No. | Name
11 | Liquid pipe needle valve
12 | Filter dryer
13 | Sight glass
14 | Liquid pipe temperature sensor
15 | Electronic expansion valve (EEV)
16 | Low pressure needle valve
17 | Evaporator
18 | Indoor fan
19 | Liquid distributor
20 | Low pressure sensor
21 | Suction temperature sensor
Notes: This section uses a Huawei air conditioner as an example to describe the layout of main components of the air-cooled air conditioner. The layout varies according to the model of the air conditioner from different vendors. The actual layout prevails.

## Slide 19: Main Components (1)
Four main components of refrigerating system
  Compressor: The compressor is the core of the refrigeration cycle and is a power unit for refrigerant to circulate inside the system.
  Condenser: Under the effect of condensing medium, the condenser liquidizes the superheat saturated steam discharged by the compressor.
  Expansion valve: used for throttling. It is a regulating device for circular flow of refrigerant.
  Evaporator: The liquid refrigerant that is throttled absorbs heat and evaporates in the evaporator to cool down cooled materials, so as to achieve the objective of refrigeration.
Scroll compressor
Condenser
Electronic expansion valve
Evaporator
Notes: There are 5 types of compressors used in refrigeration and air conditioning industry: reciprocating, screw, rotary, scroll compressor and centrifugal compressor, reciprocating compressor is a kind of widely used in small and medium-sized commercial refrigeration system. Screw compressors are mainly used in large commercial and industrial systems. Rotary compressor, scroll compressor is mainly used for household and small capacity, commercial air-conditioning unit, centrifugal compressor is widely used in large buildings air conditioning system.
According to the different cooling medium, the condenser can be divided into two types: water cooled type and air cooled type. Water cooled condenser uses water as the cooling medium, take away the heat by the water; air cooling condenser uses air as the cooling medium, take away the heat by the air.
Expansion valve can be divided into thermal expansion valve, electronic expansion valve, expansion valve is divided into two types - thermal and electronic. Thermal expansion valve not only can control the fluid volume of evaporator, but also throttling saturated liquid refrigerant, thermal expansion valve are divided into internal and external balance according to the structure; electronic expansion valve is mainly used in variable frequency air conditioning system;
According to the different types of the cooling medium, the evaporator can be divided into two categories: the type of cooling air evaporator and the type of cooling liquid evaporator.

## Slide 20: Main Components (2)
Filter dryer
Oil-gas separator
Liquid storage tank
Common auxiliary parts of refrigerating system
  Oil-gas separator: It is used to separate the lubricant brought out due to exhaustion of the compressor and brings back the separated lubricant to the compressor.
  Liquid storage tank: It is used to store excessive refrigerant in the system and guarantee that the refrigerant entering the expansion valve is liquid.
  Filter dryer: It is used to absorb moisture and filters out impurities in the refrigerating system.
  Sight glass: It is used to check whether water exists in the refrigerating system and observe the state of refrigerant.
  Solenoid valve: It is used prevent slugging due to migration of refrigerant when the air conditioning unit is powered off.
  Fan: Accelerating the air flow and improving the heat transfer capability of the heat exchanger.
Sight glass
Solenoid valve
Fan
Notes: The oil gas separator and liquid storage tank, 25 and 35 kW air conditioner have these components, because these air conditioner use variable frequency compressor. So this kind of compressor is small. So we need oil gas separator and liquid storage tank.
Other components such as high pressure switch, temperature switch, temperature sensor, differential pressure switch, pressure sensor, condensate pump, etc.

## Slide 21: Main Components (3)
Low temperature components - If we use air conditioner in lower temperature environments, we require a low temperature components to improve the continuous low pressure caused by low temperature starting. By adding low temperature components, the air conditioner can operate normally.

## Slide 22
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
  Basic Principles
  Components
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 23: Basic Principles (1)
The chiller uses the vapor-compression refrigeration principle to produce low-temperature water (called chilled water), and distributes the low-temperature water to the indoor unit (fan coil). The hot air in the room flows through the surface of the fan coil to reduce the temperature.
After heat absorption, the temperature of the chilled water increases and the water flows back to the chiller. The preceding process is repeated.
Condenser
Compressor
Expansion valve
Evaporator
Chilled water pump
Fan coil
Electromagnetic three-way valve
Fan coil
Electromagnetic three-way valve
Fan coil
Electromagnetic three-way valve
Outdoor unit
Indoor unit
Chilled water supply
Chilled water return
Indoor unit
Liquid distribution unit (LDU)
Outdoor unit
Notes: LDU: evenly distributes the low-temperature chilled water to each indoor unit. An LDU is required if there are multiple indoor units.

## Slide 24: Basic Principles (2)
Air-cooled chilled water
  Device refrigerant: chilled water
  Application scenarios: large and medium data centers
  Characteristics:
    Not requiring a cooling tower, easy to install, easy to move, and suitable for occasions where water is scarce and where a water tower is absent;
    Low-noise fan motor, excellent cooling and condensation effects, and stable throttling body;
    High EER value, low noise, and stable operation.
Returned chilled water
Supplied chilled water
Flow direction of the refrigerant
Compressor
Airflow direction
Expansion valve
Condenser
Filter dryer
Evaporator
Fan

## Slide 25: Basic Principles (3)
Water-cooled chilled water
  Device refrigerant: chilled water
  Application scenarios: large and medium data centers
  Characteristics:
    Centralized cooling and high refrigeration efficiency;
    Efficient heat transfer/exchanging device used, less cold loss, easy oil returning, and heat pipes not easily cracking;
    Central air conditioning system used, and a need to consider the problem that chilled water cannot be provided in winter.
Returned chilled water
Supplied chilled water
Flow direction of the refrigerant
Compressor
Expansion valve
Condenser
Filter dryer
Evaporator
Chilled water back
Chilled water out

## Slide 26: Basic Principles (4)
Condenser types: air-cooled condenser and water-cooled condenser
Evaporator
Expansion valve
Air-cooled condenser
Compressor
Chilled water return
Chilled water supply
Chilled
water
pump
Compressor
Expansion valve
Chilled water return
Chilled water supply
Chilled
water
pump
Evaporator
Water-cooled condenser
Cooling tower
Cooling water
pump
Notes: Cooling tower mode: The cooling water is directly in contact with the air after the water temperature increases. The air absorbs the heat of the water. After the water temperature decreases, the cooling water flows back to the water-cooled condenser and can be used again.

## Slide 27
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
  Basic Principles
  Components
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 28: Components of a Huawei Chilled Water Air Conditioner
No. | Name
A | Chilled water inlet
B | Chilled water outlet
1 | Balance valve or isolation valve
2 | Water strainer
3 | Isolation valve
4 | Soft connection
5 | Chilled water inlet and outlet pipe connectors
6 | Chilled water valve
7 | Heat exchanger
Notes: This section uses a Huawei air conditioner as an example to describe the layout of some components of the chilled water air conditioner. The layout varies according to the model of the air conditioner from different vendors. The actual layout prevails.

## Slide 29: Main Components (1)
Main components of refrigerating system
  Two way valve - The water flow into the air conditioner is adjusted continuously according to the change of the thermal load, and the temperature is accurately controlled;
  Fan - Accelerating the air flow and improving the heat transfer capability of the heat exchanger;
  Surface air cooler - A component that controls the indoor temperature and humidity by exchanging heat between chilled water and indoor air.
Actuator
Valve body
Fan
Surface air cooler
Two way valve

## Slide 30: Main Components (2)
Common auxiliary components
  Power supply unit - Provide stable power supply to the fan;
  Condensate water pump - Drain condensate water from the system;
  Float - Used to control condensate water level.
Other components
  Water sensor
  Temperature sensor
  Air filter
  Electric heater
  Electrode humidifier
Power supply unit
Condensate water pump
Float

## Slide 31
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
  Basic Principles
  Components
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 32: Basic Principles (1)
Evaporative cooling principle:
  In nature, liquids, such as water, absorb heat from the air during evaporation, causing the air temperature to drop. Water evaporates at any temperature and absorbs heat from the air, causing the air temperature to drop. Evaporative cooling is an isenthalpic process of humidifying and cooling air.
Evaporative cooling phenomena:
Notes: Note that the total amount of heat absorbed is very large. If 1 g water is added to each kg of air, the air temperature decreases by 2.5°C after the water evaporates.
Enthalpy is an important state function that measures the energy of a material system in thermodynamics.
If a system absorbs heat, the enthalpy value increases. If the system releases heat, the enthalpy value decreases.
For simple state changes of a homogeneous system, the enthalpy of high-temperature materials is higher than that of low-temperature materials because of the temperature rise of the system.
During phase changes, heat is absorbed when solids change to liquids, solids change to gases, and liquids change to gases. Therefore, the enthalpy values of the same material in different aggregation states at the same temperature are not equal: H (g) > H (l) > H (s).
For the chemical reaction when the temperature remains constant, if the reactant absorbs heat, the enthalpy of the product is higher than that of the reactant. If the reactant releases heat, the enthalpy of the product is lower than that of the reactant.

## Slide 33: Basic Principles (2)
In the indirect evaporative cooling process, the cooled air and water obtained by (direct) evaporative cooling are transferred to the air to be processed through an indirect-contact air-to-air heat exchanger, so as to obtain air with temperature reduced but moisture content unchanged. This is an iso-humid process of cooling air.
(4) Outlet of secondary air
Water
spraying
Inlet of
primary air
(2) Outlet of
primary air
(3) Inlet of
secondary air
T4
T3
T1
T2
1—2: Iso-humid process of cooling, indirect cooling
3—4: Isenthalpic process of humidifying, direct evaporative cooling
Conceptual diagram of an indirect evaporative cooling system
Notes: Primary air is air that is indirectly cooled.
Secondary air is air cooled by direct evaporation.

## Slide 34: Basic Principles (3)
Based on the outdoor fresh air temperature and humidity and IT load, an air conditioner works in three modes to implement on-demand cooling.
Dry mode
Wet mode
Hybrid cooling mode
Working Mode | Outdoor Ambient Temperature (100% Load) | Fan | Water Pump | Compressor
Dry mode | Dry bulb temperature ≤ 16°C | ON | OFF | OFF
Wet mode | Dry bulb temperature > 16°C; wet bulb temperature ≤ 19°C | ON | ON | OFF
Hybrid cooling mode | Wet bulb temperature > 19°C | ON | ON | ON
Outdoor fresh air
Outdoor air exhaust
Indoor air return
Indoor air supply
Outdoor fresh air
Outdoor air exhaust
Indoor air return
Indoor air supply
Outdoor fresh air
Outdoor air exhaust
Indoor air return
Indoor air supply

## Slide 35
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
  Basic Principles
  Components
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 36: Components of a Huawei Indirect Evaporative Cooling Air Conditioner
No. | Name
1 | Compressor
2 | Shock-absorbing corrugated pipe
3 | High pressure sensor
4 | High pressure switch
5 | Discharge temperature sensor
6 | One-way valve
7 | Exhaust pipe needle valve
8 | Exhaust fan
9 | Heat exchanger
No. | Name
10 | Liquid pipe needle valve
11 | Liquid pipe temperature sensor
12 | Strainer
13 | EEV
14 | Low pressure needle valve
15 | Indoor fan
16 | Gas-liquid separator
17 | Low pressure sensor
18 | Suction temperature sensor
Notes: This section uses a Huawei air conditioner as an example to describe the layout of some components of the indirect evaporative cooling air conditioner. The layout varies according to the model of the air conditioner from different vendors. The actual layout prevails.

## Slide 37: Components
Heat exchanger core: cross-flow heat exchanger, improving heat exchange efficiency
Fan: accelerates air flow and improves the heat exchange capability.
Nozzle: ensures the spray pressure and improves the spray effect.
Water tank: stores water and provides spray water for a certain period of time.
Shock-absorbing pipe: reduces pipe vibration to prevent pipe cracks during transportation and operation, improving the unit reliability.
Differential pressure switch: detects the differential pressure between the front and rear of the internal circulation air filter to determine whether the air filter is dirty or blocked.
Heat exchanger core
Fan
Nozzle
Water tank
Shock-absorbing pipe
Differential pressure switch
Notes: Other components include the auxiliary cooling system, pipes, pressure sensor, temperature and humidity sensor, and one-way valve.

## Slide 38
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 39: Refrigerant Pump Cooling Technology
When the outdoor temperature is higher than 20°C, the conventional mechanical cooling solution is adopted. The compressor works properly and the refrigerant pump does not work.
When the outdoor temperature is lower than 10°C, the compressor stops and the refrigerant pump starts cooling.
When the outdoor temperature is greater than or equal to 10°C and less than or equal to 20°C, the refrigerant pump and compressor start cooling at the same time, enabling the hybrid cooling mode to save energy.
Evaporator
Compressor
One-way valve
One-way valve
Liquid storage tank
Condenser
Refrigerant pump
Refrigerant pump cooling cycle
Compressor cooling cycle
Notes: Refrigerant pump: refers to a pump lined with fluoroplastics, which is widely used in chemical production and transports strong corrosive media for a long time in the environment of –20°C to +150°C.

## Slide 40: Fan Wall Cooling Technology
The fan wall technology is an energy-saving technology that uses free cooling sources. Based on the indoor and outdoor temperature difference, the outdoor cold air is taken into the equipment room to absorb heat through the process of air intake, pre-processing, fan wall, air exhaust, and air return. In this way, partial or complete free cooling without mechanical cooling is implemented for the equipment room, which saves energy.
The fan wall technology, with multiple small fans arranged in order, replaces a single large fan in a conventional air handler, so that airflow organization is more even and fan energy consumption is lower.
Notes: Fan Wall Data Center Airflow Organization Research And Energy Consumption Analysis: The fan wall system consists of the chilled water cooling system and fresh air system. There are four modes: chilled water cooling mode, fresh air and chilled water parallel mode, fresh air mode, and fresh air mixture cooling mode.
Different vendors may adopt different fan wall modes.
Yahoo's Compute Coop is an early and well-known data center that uses the fan wall technology. In some areas in China, the fan wall technology fails to be promoted due to air quality problems. Some equipment rooms in Baidu Cloud Computing (Yangquan) Center use fan walls and high-temperature corrosion-resistant servers.

## Slide 41: Backplane Heat Pipe Air Conditioner
The cooling unit is distributed to the cabinet backplane in the internal area. Based on the heat pipe principle, the liquid working medium absorbs heat at the cabinet backplane in the indoor area and evaporates to gas, which rises to the outdoor condenser. After condensation, the gas working medium releases heat to the outdoor environment and becomes liquid, which flows back to the indoor environment under gravity. In this way, the indoor heat is transferred to the outdoor environment to complete the cooling cycle.
Water fluorine heat exchanger
Air return pipe
Gas hose
Backplane
Cabinet
Liquid hose
Liquid supply pipe
Ground
Chilled
water
Notes: A heat pipe is a heat transfer element with extremely high thermal conductivity. It transfers heat by evaporation and condensation of liquids in a fully enclosed vacuum pipe. A heat exchanger formed by heat pipes has advantages such as high heat transfer efficiency, a compact structure, and small fluid resistance.
This air conditioner type prevents water from entering the cabinet area and eliminates water leakage risks.
There are a large number of indoor units (backplanes), pipes, and connectors, and the O&M workload is heavy.

## Slide 42: Liquid Cooling Technology
Cold plate liquid cooling
  An LDU is configured on the liquid cooling cabinet to provide water inlet and outlet pipes. The LDU is connected to the internal cold plate pipes in the liquid-cooled compute nodes to implement liquid cooling circulation in the compute nodes.
Immersion liquid cooling
  Specific coolant is used as the heat dissipation medium. Immerse IT equipment in the coolant to take away heat through coolant circulation.
Spray liquid cooling
  Insulated non-corrosive coolant is sprayed onto the surface of a heating device (or the extended surface in contact with the heating device) through the spray plate on the server box for heat exchange.
Cooling system (including the primary tube)
CDU system and cooling medium
Secondary tube between the CDU and cooling cabinet
Huawei FusionServer cooling cabinet
Air
conditioner
Notes: The data center construction cost is reduced by 60%: Raised floors, heat dissipation channels, and server spaces are not required.
Energy consumption of cooling is reduced by 90%: Fans and heat sinks are removed from servers, and no air conditioner humidifier is required in the equipment room, reducing noise in the equipment room.
The total energy and maintenance costs are reduced by 50%: The hardware service life is prolonged and the number of components is reduced.
High reliability is required. Leakage risks exist.

## Slide 43
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 44: Huawei Precision Air Conditioner Series
NetCol5000-A011
NetCol5000-A020
NetCol5000-A025
NetCol5000-A035
NetCol5000-A042
NetCol5000-A050
NetCol5000-A
NetCol5000-C
NetCol5000-C030
NetCol5000-C065
NetCol8000-A
NetCol8000-A(045, 090)
NetCol8000-A(050, 100)
NetCol8000-C
NetCol8000-C(070-260) NetCol8000-C(070, 130, 190) NetCol8000-C(050–150)
In-row precision air conditioner
(11–65 kW)
In-room precision air conditioner (45–260 kW)
NetCol8000-E
NetCol8000-E220
Indirect evaporative cooling air conditioner (220 kW)

## Slide 45: Huawei Outdoor Unit Series
Main functions
  The outdoor unit controls the fan speed based on the condensing pressure to implement variable frequency speed control.
  The outdoor unit provides protection against overheating for fans.
  The driver provides a screen manipulator for keys and nixie tubes to meet commissioning requirements.
  Indoor and outdoor units are connected using signal cables. The outdoor unit is started or shut down as instructed by the indoor unit.
Dual-fan NetCol500
NetCol500-A026
NetCol500-A032
NetCol500-A036
NetCol500-A038
NetCol500-A072
NetCol500-A088
Single-fan NetCol500

## Slide 46
(Single)Which of the following is not one of the four major components of an air-cooled air conditioner?
  Compressor
  Evaporator
  Fan
  Condenser
(Multiple)Which of the following are the performance features of an air conditioner in an equipment room?
  Small air volume and large enthalpy difference
  Cooling throughout the year
  High reliability
  Various air supply modes
Notes: Answer to question 1: C. Four major components of an air conditioner are the compressor, condenser, expansion valve, and evaporator.
Answer to question 2: B, C, and D. Precision air conditioners feature small enthalpy difference and large air volume. Cooling can be implemented throughout the year. In addition, to ensure the environment for equipment in the equipment room, high reliability and redundancy design are required. In addition, air conditioners in an equipment room support multiple air supply modes, including upward air supply, downward air supply, and horizontal air supply.

## Slide 47
(Single)When the indirect evaporative cooling system works in dry mode, there is an iso-humid process of cooling.
  True
  False
Notes: Answer to question 3: A

## Slide 48
Overview of Data Center Air Conditioners
Air-Cooled Precision Air Conditioner
Chilled Water Precision Air Conditioner
Indirect Evaporative Cooling Air Conditioner
Other Cooling Solutions for Equipment Rooms
Introduction to Huawei Air Conditioners

## Slide 49
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 51
Shenjutao/WX352174
2017.07.01
New
HCIA-DCF
Wang Cong/wx760444
2020.4
Li Shaofeng/l00486775
Notes: 2015.7.4
  调整版权和页码对齐，位于参考线8.5到8.9之间。
2015.7.14
  新增更多信息和推荐的样例。
2015.8.3
  胶片主体和备注页，段落设置为“允许标点溢出边界”。
2015.8.4
  删除缩略语页。
2015.9.2
  新增备注页页眉，居于备注页正上方，显示本章标题。
2015.9.14
  删除“谢谢”那页的白色“谢谢”。
2017.11.8
  调整母版中标题宽度。