## Slide 1: Basic Knowledge of Monitoring Systems

## Slide 2
This chapter describes basic knowledge about the monitoring system, including interfaces and common protocols of the monitoring system and data center infrastructure monitoring modes.

## Slide 3
Upon completion of this course, you will be able to:
  Describe basic interfaces and communication protocols.
  Describe the overall architecture of the monitoring system.

## Slide 4
Introduction to the Monitoring System
Basic Interfaces and Communication Protocols
Introduction to the Data Center Monitoring System

## Slide 5: What is Power and Environment Monitoring System
Power and environment monitoring system
Power equipment
Environmental conditions
Power equipment
UPS
Diesel Generator
High-voltage and low-voltage power distribution
Mains power distribution
Batteries
Environmental conditions
Audio and video
Access control device
Air conditioner
Smoke sensor
Temperature
Humidity
Infrared sensor
Water sensor
The power and environment monitoring system is the short name of the power and environment centralized monitoring system.

## Slide 6: Overview of the Monitoring System
Air conditioner
UPS
Video
PDF
PDU
Infrastructure
Access control device
Smoke sensor
Monitoring System
Southbound interface
Building
Fire fighting
Lighting
Security protection
Power
Third-party system
SNMP
SNMP
TXT
Portal
NMS/L2 level
SNMP
Modbus
Telecom protocol
Northbound interface
Integrated interface
General
control center
System functions
Monitoring
functions
Management
functions

## Slide 7: Application Scenarios of the Monitoring System
Equipment room
Unattended transformer substation
Transport node station
Wireless base station
Oil field
Protected agriculture
Food and drug warehousing
Power and environment monitoring system

## Slide 8: Development Trend
With the development of technologies, data center staff want to reduce inspection times of on-duty staff, reduce the workload of data center maintenance and management staff, and improve system stability by monitoring system equipment and environment.
  Unified monitoring: The monitoring system of equipment rooms is integrated with enterprise IT operation and maintenance (O&M) management systems (such as systems of service monitoring, server monitoring, and network monitoring) to form a complete management system.
  AI energy conservation: drives data center energy efficiency diagnosis and optimization to continuously reduce energy consumption. It saves energy by monitoring and managing IT equipment chips and site environment.
  Mobile inspection technology: Scheduled inspection of equipment rooms is one of the most important routine O&M tasks of a data center. Mobile inspection reduces the workload of staff and improves the accuracy of inspection data.
  Fiber grating temperature measurement technology: An electrical equipment failure can cause insulation performance deterioration or even breakdown, damaging the equipment. Common measurement methods cannot accurately monitor the equipment operating temperature online. Fibers can overcome this difficulty and ensure equipment security.

## Slide 9: Intelligent Building Monitoring System
The main functions of the intelligent building monitoring system are integrated monitoring, linkage, and management of the systems under real-time monitoring system in a building.
The intelligent building monitoring system focuses on the overall management of a building, and the power and environment monitoring system focuses on the management of in-house equipment.
Power supply system
Lighting system
Air supply and exhaust systems
Water supply and drainage systems
Elevator system
Air conditioning system
Chiller plant system
Heating plant system
Notes: Intelligent building: The building management staff only need to perform jumpering between corresponding points and equipment in the central control room to connect the equipment to the building's cabling system for control and management.
Power supply system: Power supply is an important indicator for evaluating the service quality of an intelligent building. Generally, the power supply transformers, and power supply parameters on both the high-voltage side and the low-voltage side (or only one item of them) need to be monitored.
Lighting system: The system is monitored to save energy. Lighting is automatically controlled based on the preset schedule program. The lighting system mainly includes lighting in public areas, living areas, office areas, and streets, as well as emergency lighting and flood lighting.
Air supply and exhaust systems: The systems are monitored and managed in a unified manner. They run according to the preset schedule program in control of air supply and exhaust fans, parameter monitoring, alarming, and logging.
Water supply and drainage systems: consist of domestic water supply (cold and hot water) and sewage drainage. They provide constant pressure water supply, indicate and alarm the sewage tank liquid level. They also implement various scheduled and cyclic operations of water supply and drainage pumps, including water pump control, water flow detection, water pressure monitoring, sewage liquid level detection, and sewage pump control.

## Slide 10
Notes: Elevator system: Passenger elevators and escalators are monitored. Monitored objects generally include elevator start-stop control, running status, elevator door status, floor indication, failure alarm, and emergency alarm.
Air conditioning system: Air conditioning units, fresh air handling units, variable air volume (VAV) units, and fan coil units are monitored. Controlled objects mainly include temperature and humidity adjustment, preset time schedule and automatic start and stop.
Chiller plant system: provides cold sources for the air conditioner system. It consists of chillers, cooling water circulation pumps, cooling towers, chilled water circulating pumps, water supply pumps, and electric butterfly valves.
Heating plant system: provides heat sources for the air conditioning system. It consists of boilers, plate heat exchangers, chilled water circulating pumps, water supply pumps, and electric butterfly valves.

## Slide 11
Overview of the Monitoring System
Basic Interfaces and Communication Protocols
  Basic Concepts
  Common Protocols and Interfaces
  Parameter Settings of Common Protocols
Introduction to the Data Center Monitoring System

## Slide 12: Basic Concepts
Interface: connection mode between two hardware devices.
Protocol: a group of conventions that both parties involved in communication must observe, for example, how to establish a connection and how to identify each other. Both parties can communicate with each other only after they observe the conventions.
For example, mouse and USB drive are devices that use USB ports. These devices must comply with USB port specifications before they can be used over USB ports.
Notes: OPC: OPC is a communication specification in industrial control, including an OPC server program and an OPC client program. The specification ensures that the OPC server can be accessed by the OPC client.
Simple network management protocol (SNMP). SNMP consists of a group of network management standards, including an application layer protocol, database schema, and a a group of resource objects. SNMP supports the network management system (NMS) and is used to monitor whether devices connected to the network attract attention of management.
The Modbus protocol is a general language used on electronic controllers. Over this protocol, controllers can communicate with each other or communicate with other devices through network (for example, Ethernet). Modbus has become a general industrial standard. Over Modbus, control devices produced by different vendors can be connected to the industrial network for centralized monitoring.

## Slide 13: Basic Concepts
Common interface types
  DB9, RJ45, and cord end terminal.
Transmission modes
  RS232, RS485, RS422, and FE.
Protocol Type
  SNMP, Modbus, telecom protocol, OPC, and other protocols.
Notes: OPC: OPC is a communication specification in industrial control, including an OPC server program and an OPC client program. The specification ensures that the OPC server can be accessed by the OPC client.
Simple network management protocol (SNMP). SNMP consists of a group of network management standards, including an application layer protocol, database schema, and a a group of resource objects. SNMP supports the NMS and is used to monitor devices connected to the network attract attention of management.
The Modbus protocol is a general language used on electronic controllers. Over this protocol, controllers can communicate with each other or communicate with other devices through network (for example, Ethernet). Modbus has become a general industrial standard. Over Modbus, control devices produced by different vendors can be connected to the industrial network for centralized monitoring.
Cord end terminal: Air interfaces belong to cord end terminals. Cord end terminals are accessories used to implement electrical connection and belong to the scope of connector in terms of industry.

## Slide 14
Overview of the Monitoring System
Basic Interfaces and Communication Protocols
  Basic Concepts
  Common Protocols and Interfaces
  Parameter Settings of Common Protocols
Introduction to the Data Center Monitoring System

## Slide 15: Comparison of Common Protocols
Protocol Type | Feature | Transmission Mode | Category | Applicable Scope | Advantage | Disadvantage
Modbus | Field bus protocol, master/slave mode | Serial transmission, supporting loading of RS232/RS485/RS422 | ModBus-RTU ModBus-ASC ModBus-TCP | Air conditioners, UPSs, ammeters, humidifiers, PDUs, and controllers | Standard and open, supporting multiple electrical interfaces; the frame format is simple and easy to use. | Master/slave mode, providing low efficiency
SNMP | Network management protocol | Used on TCP/IP networks in UDP mode. | SNMPV1.0 SNMPV2.0 SNMPV3.0 | Air conditioners, UPSs, and PDUs | Complying with the OSI model, open protocol, and implementing management relying on network; the protocol is widely used; security is high. | The number of devices is large and the efficiency of query among much data is low; processing is complex.
Telecom protocol | Field bus protocol, master/slave mode | Serial transmission, supporting loading of RS232/RS485/RS422 | Frontend intelligent monitoring equipment communication protocol for power supply, air conditioners, and integrated environment management system of telecommunication offices (sites) | Based station air conditioners and base station power supply | Open protocol, supporting multiple electrical interfaces | The format is complex and the protocol is not universal.
Notes: SNMP is used to manage nodes on the network (including workstations, routers, switches, hubs, and other peripherals). At present, three SNMP versions are defined: SNMP v1, SNMP v2, and SNMP v3. SNMP v1 and SNMP v2 have many characteristics in common. Based on earlier versions, SNMP v3 adds the security and remote configuration capabilities.
SNMP v1uses only one security policy, namely community name. A community name is similar to a password. The agent can be set to answer questions from the managers whose community names can be accepted. This makes it easy for people to intercept community names or passwords. SNMP v2 adds extra security. Except the destination address, all packet information is encrypted.

## Slide 16: Comparison of Common Transmission Modes and Interfaces
Transmission Mode | Number of Pins | Electrical Characteristic | Transmission Mode | Transmission Distance | Transmission Rate | Advantage | Disadvantage
RS232 | Standard 25-pin, common 3-pin | ±15 V | Full duplex, single point | 15 m | 20 K | It is easy to obtain tools. | The distance is limited, networking is unavailable, and the transmission mode is susceptible to interference.
RS485 | Standard 4-pin and 2-pin, common 2-pin | TTL (±2 to ±6) | Half duplex, master/slave | 1200 m | 10 M | 2-pin interfaces are widely used, networking is convenient, and the anti-interference capability is provided. | The distance is large and resistance must be matched at a high rate.
RS422 | Standard 4-pin | TTL (±2 to ±6) | Half duplex, master/slave | 1200 m | 10 M | The anti-interference capability is provided and networking is available. | The distance is large and resistance must be matched at a high rate. The number of slave nodes is 10, which is smaller than that of RS485. The number of cores is greater than that of RS485.
FE | Standard 8-pin | TTL | Full duplex, multi-master | 100 m | 10 M | The transmission rate is high, the efficiency is high, and flexible networking is provided. | The networking cost is high.
Common interface forms:
DB9
DB25
Crimp terminal
RJ45
RJ12
Notes: RJ12 interfaces are 6-pin interfaces. The lines matching RJ12 are RJ12 plug lines, which are commonly telephone lines.

## Slide 17
Overview of the Monitoring System
Basic Interfaces and Communication Protocols
  Basic Concepts
  Common Protocols and Interfaces
  Parameter Settings of Common Protocols
Introduction to the Data Center Monitoring System

## Slide 18: Parameter Settings - SNMP
SNMP
Notes: The IP address of a computer is the only identifier of the computer on the network. On any network, IP addresses cannot be the same.
A subnet mask is used by the server to differentiate the network segment of an IP address.
A default gateway refers to the default machine through which clients search on the network.

## Slide 19: Parameter Settings - Modbus
Modbus
Notes: Modbus RTU: If a device needs to be connected to the NMS over an RS485 monitoring cable, select Modbus RTU for Protocol.
Baud rate: Set Baud rate based on actual conditions. The baud rate must be the same as that on the NMS.
Comm address: Communication address planned for a device. Based on this address, the NMS communicates with the device.

## Slide 20: Parameter Settings - Dry Contact
Dry contact
Notes: A dry contact is an electrical switch. It can be enabled or disabled. There is no polarity between dry contacts and dry contacts can be exchanged. Common dry contact signals include various switches such as limit switch, travel switch, foot switch, rotary switch, temperature switch, and fuel level switch.

## Slide 21
Overview of the Monitoring System
Basic Interfaces and Communication Protocols
Introduction to the Data Center Monitoring System
  System Architecture
  Application Scenarios
  Monitoring Implementation Mode

## Slide 22: Composition of Hardware Devices
Signal transmission
Monitoring center
Signal transmission
Information collection
Server
Server
Server
Client
Client
Basic devices

## Slide 23: Software Architecture
UI
Applications and services
Basic framework
Access layer
Southbound embedded protocol plug-in
Basic modules
Web integrated framework
Applications and services
SSO
Portal container
Integration UI
Fault management
Work order management
Communication bus
Lightweight Web running container
Modbus
Telecom
SNMP
...
Database service
Security/log
UI component
Message service
Performance management
Configuration management
Software management
Energy efficiency management
Capacity management
Real-time monitoring
Report management
Inventory monitoring
Notes: Generally, the monitoring software adopts the B/S architecture, which consists of the access layer, public framework, applications and services, and UI layer.
The monitoring software runs on the operating system (OS) based on SUSE10/SUSE11.
Users can access the server over Web on terminals based on Windows OS (to ensure data transmission security, the monitoring software adopts SSL to encrypt transmission).

## Slide 24
Overview of the Monitoring System
Basic Interfaces and Communication Protocols
Introduction to the Data Center Monitoring System
  System Architecture
  Application Scenarios
  Monitoring Implementation Mode

## Slide 25: Data Center Application Scenario
The monitoring system helps users quickly locate faults by monitoring infrastructure of the data center, supports centralized configuration and status monitoring for basic devices in the data center, and implements remote refined management for the data center.
The monitoring system can be deployed in medium and large modular data centers, small modular data centers, and container data centers.

## Slide 26: Medium and Large Modular Data Centers
Medium and large modular data centers are a series of complete data center solutions. The solutions are applicable to quick deployment of medium and large data centers of operators and large corporate customers.
Air conditioner
Temperature/humidity sensor
Camera
Smoke sensor
Access control device
Water sensor

## Slide 27: Small Modular Data Centers
Small modular data centers are mainly used in cloud hosts in parks, branches of large enterprises, small and medium enterprises, e-government networks, education, healthcare, and data equipment rooms of financial branches.
Collector
Switch
Server
Firewall
Monitoring function
Small Module Data Center

## Slide 28: Container data center
Battery cabinet
Battery cabinet
Air conditioner cabinet
Fire control cabinet
Battery compartment
Dust filter
Transducer
Fire fighting monitoring component
UPS compartment
Serial hub
Cable distribution box
Monitoring module box
DDF module
Notes: Container products can be used in the following scenarios:
  Container products are independently used outdoors and no local monitoring center is provided. In this scenario, no distributed monitoring node is provided and only the centralized management platform installed on the rack server in containers needs to be used.
  Container products are used outdoors. Distributed nodes are installed on the rack server installed in containers and the centralized management platform is installed on the general server of the monitoring center.

## Slide 29
Overview of the Monitoring System
Basic Interfaces and Communication Protocols
Introduction to the Data Center Monitoring System
  System Architecture
  Application Scenarios
  Monitoring Implementation Mode

## Slide 30: Subsystem Monitoring
Monitoring system
Power supply and distribution equipment
Cooling equipment
Environment equipment
Security protection equipment
Diesel generator
UPS
Battery
...
Refrigerating unit
Precision air conditioner
Cooling capacity meter
...
Sensor
Alarm device
Fire fighting system
Camera
Access controller
...
...

## Slide 31: Subsystem Monitoring Implementation Mode (1)
Device Name | Object Monitored by NetEco | Monitoring Implementation Mode
Diesel generator | Operating status, operation parameters, alarms, and remote management; operation parameters of remote management provided by protocols for various devices. | Based on different interfaces provided by the devices, the solution provides two network connection modes. Devices supporting Modbus or Telcom protocol are connected to the serial server or monitoring system collector that provides transparent transmission capability over RS485. Devices supporting SNMP are connected to the monitoring system over the FE interface.
ATS and STS |  | 
UPS |  | 
Battery and battery cabinet |  | 
UPS output cabinet |  | 
PDU |  | 
PDB |  | 
RPDU |  | 
Power supply and distribution equipment

## Slide 32: Subsystem Monitoring Implementation Mode (2)
Device Name | Object Monitored by NetEco | Monitoring Implementation Mode
Refrigerating unit | Operating status, operation parameters, alarms, and remote management; operation parameters of remote management provided by protocols for various devices. | Based on different interfaces provided by the devices, the solution provides two network connection modes. Devices supporting Modbus or Telcom protocol are connected to the serial server or collector that provides transparent transmission capability over RS485. Devices supporting SNMP are connected to the monitoring system over the FE interface.
Precision air conditioner |  | 
Cooling capacity table |  | 
In-row air conditioner |  | 
Humidifier |  | 
Refrigerating equipment

## Slide 33: Subsystem Monitoring Implementation Mode (3)
Device Name | Object Monitored by NetEco | Monitoring Implementation Mode
Smoke sensor | Monitor the smoke concentration in an equipment room or module. | The smoke sensor is connected to the collector over the DI interface.
Temperature / humidity sensor | Monitor temperature and humidity in an equipment room or module. | The temperature and humidity sensor is connected to the collector over the RS485 interface.
Water sensor | Monitor liquid leakage in an equipment room or module. | The water sensor is connected to the collector over the DI interface.
Audible and visual alarm device | When an alarm is generated in an equipment room or module, the audible and visual alarm device in the equipment room or module produces sound or light, prompting the user to handle the alarm. | the collector over the skylight controller.
Environment equipment

## Slide 34: Subsystem Monitoring Implementation Mode (4)
Device Name | Object Monitored by NetEco | Monitoring Implementation Mode
Hydrogen detection system | Monitor whether hydrogen exists in an equipment room or module and prevent safety accidents such as fire due to high concentration of hydrogen. | The hydrogen detection system is connected to the collector through dry contacts.
Fire fighting system | Control fire extinguishing equipment in an equipment room to put out fire. | The fire fighting system is connected to the collector through dry contacts.
Environment equipment

## Slide 35: Subsystem Monitoring Implementation Mode (5)
Device Name | Object Monitored by NetEco | Monitoring Implementation Mode
Camera | Real-time situation in an equipment room or module. | Cameras of the standard configurations are directly connected to a switch over the FE interface and are supplied with power in POE mode to view video information in real time.
NVR | Configure and manage cameras. | The NVR is used to store HD images and provide large-scale storage medium to store videos on a long-term basis. The videos are stored in different files based on time segment.
Equipment room access controller | Control and manage card readers. | Equipment room access controllers are connected to the monitoring system over the FE interface.
Security protection equipment

## Slide 36
(Short Answer Question)What are differences between SNMP and Modbus?
(Short Answer Question)Which scenarios can the power and environment monitoring system be used in?

## Slide 37
Basic Interfaces and Communication Protocols
Subsystem Monitoring of Data Centers
Technical Indicators and Environment Standards

## Slide 38
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 40
HCIA-DCF
V2.0
Qian Hui
2015.01.25
Li Shaofeng/l00486775
New
Wang pulin/wx763618
2020.12
Li Shaofeng/l00486775
Update
Notes: 2015.7.4
  调整版权和页码对齐，位于参考线8.5到8.9之间。
  调整编辑框行距为单倍行距。
2015.7.9
  删除此页课程版本后的“ISSUE”。
  新增“产品版本”和“课程版本”的示例。
2015.8.3
  调整母板主体和备注，段落格式为“允许标点溢出边界”。
2015.8.4
  删除缩略语页；
  重命名版式“8#空白”为“8#仅标题”。
2015.9.2
  新增备注模板，备注页正上方添加页眉，显示本章标题。
2015.9.14
  删除“谢谢”那页的白色“谢谢”。