## Slide 1: Functions and Features of Monitoring Systems

## Slide 2
This slides describe the main features and functions of the monitoring system, including the general control center and monitoring function, management function, and system function.

## Slide 3
Upon completion of this course, you will be able to:
  Describe the features and advantages of the monitoring system.
  Understand the main functions of the monitoring system.

## Slide 4
Overview of the Monitoring System
  Hierarchical Deployment
  Architecture Types
  Monitoring Features
Introduction to Main Functions
Introduction to Huawei Monitoring System

## Slide 5: Overview of the Monitoring System
Air conditioner
UPS
Video
PDF
PDU
Infrastructure
Access control device
Smoke sensor
Monitoring System
Southbound interface
Building
Fire fighting
Lighting
Security protection
Power
Third-party system
SNMP
SNMP
TXT
Portal
NMS/L2 level
SNMP
Modbus
Telecom protocol
Northbound interface
Integrated interface
General control center
System functions
Monitoring functions
Management functions

## Slide 6: Hierarchical Deployment of the Monitoring System
When multiple equipment rooms need to be monitored at the same time, hierarchical deployment is required.
Abbreviation | Full Name
SC | Supervision Center
SS | Supervision Station
SU | Supervision Unit
SM | Supervision Module
Multi-level architecture
Management layer
Collection layer
SC
SS
Device monitoring
Remote
2-level architecture
Notes: Supervision Center (SC)
Local network or network management center of the same management level
Supervision Station (SS).
Regional management and maintenance unit.
Supervision Unit (SU).
Minimum subsystem of the monitoring system. It consists of several monitoring modules and other auxiliary devices. The monitoring generally covers an independent.
communication office (site) or an independent power supply system in a large office or site.
Supervision Module (SM).
Completes specific management functions and provides corresponding monitoring information.

## Slide 7: Centralized Monitoring
Monitoring module
Power distribution box
Battery pack
UPS
T/H sensor
Branch site 1
Branch site 2
Branch site N
LAN
Server
Switch
Management center
...
Centralized monitoring involves 2-level architecture and multi-level architecture.

## Slide 8
Overview of the Monitoring System
  Hierarchical Deployment
  Architecture Types
  Monitoring Features
Introduction to Main Functions
Introduction to Huawei Monitoring System

## Slide 9: Double-Layer Architecture
Two levels architecture: that is, management layer + data collection layer
Only one monitoring station is provided.
Multiple modules or equipment rooms are allowed.
The levels of equipment rooms are not differentiated.
This is the most common monitoring system mode.
Server
Switch
Collector
Collector
Dry contact
Cabinet
Air
conditioner
ATS
T/H Sensor
Access control system
Water sensor
Smoke sensor
Camera
Notes: Typical case: An equipment room has multiple micro-modules and is monitored by one SC.
Server + collector + sensor/monitoring card.
One server serves multiple collectors.
Sensors and collectors are collectively called the data collection layer.

## Slide 10: Multi-Layer Architecture
Typical 3-level architecture, that is, SC + SS + data collection layer
Typical scenario in which the head office can directly manage branch equipment rooms.
The monitoring management system of a branch center can be relatively independent and is an integral part of the SC.
General center
Service console
Service console
Service console
Service console
Equipment room
Equipment room
Equipment room

## Slide 11
Overview of the Monitoring System
  Hierarchical Deployment
  Architecture Types
  Monitoring Features
Introduction to Main Functions
Introduction to Huawei Monitoring System

## Slide 12: Features of the Monitoring System (1)
Flexible infrastructure management capability
  Real-time device monitoring, ensuring device reliability and high utilization.
  Real-time environment monitoring, ensuring environment consistency.
  Robust security protection management, fully protecting security of devices and environments.
  Accurate energy efficiency analysis, providing customizable and diversified energy consumption statistical and analysis methods.

## Slide 13: Features of the Monitoring System (2)
Software and hardware layering
  The monitoring hardware (collector) collects data of infrastructure and sends the data and alarms to the monitoring software.
  The management software is divided into the data collection layer and the management and operation service layer.
Modular design
  Basic modules must be configured.
  Advanced modules can be generally deployed as required or selectively deployed.

## Slide 14: Features of the Monitoring System (3)
Standard network management interface
  The monitoring system can provide third-party NMSs with SNMP interfaces to meet information exchange with third-party systems. In addition, the monitoring system can provide a multi-protocol expansion mechanism to meet access of difference devices.
Flexibly configured collector
  Installation on a 19-inch cabinet is supported. The collector can be installed at the back of the cabinet to save space.
  Front and rear installation using mounting ears is supported to meet installation requirements for different product configurations.
  AI/DI expansion cards and serial expansion cards are supported.

## Slide 15
Overview of the Monitoring System
Introduction to Main Functions
Introduction to Huawei Monitoring System

## Slide 16: Monitoring System Functions
Monitoring system
Monitoring
functions
Management
functions
System functions
General
control center
Linkage control
Alarm management
Asset management
Energy consumption management
Capacity management
Operation and maintenance
(O&M) management
Log management
Rights management
System management
Service desk functions
Display functions
Real-time monitoring
Security protection management

## Slide 17: Monitoring Functions — Real-time Monitoring
The system allows users to view the running status of power supply and distribution equipment, air conditioners, security protection equipment, and fire protection equipment.
Real-time monitoring
Power supply and distribution
Air conditioning environment
Security protection
Fire protection
Uninterruptible power system (UPS), generator sets, power
distribution frames (PDFs), intelligent power distribution
units (PDUs), and batteries
Precision air conditioners, fresh air units, and cooling towers
Video surveillance subsystem and access control subsystem
Fire protection subsystem

## Slide 18: Monitoring Functions — Alarm Management
The monitoring system collects equipment information and generates warning and alarm information respectively before and after a condition is met according to preset alarm rules. Then, it displays and notifies the warning and alarm information to users.
Alarm management
Alarm browsing
Alarm analysis
Alarm handling
Alarm notification
Allows users to browse current alarms, historical alarms, and masked alarms, and view alarm details.
Classifies alarms based on certain rules to facilitate user management.
Allows users to acknowledge, clear, export, and mask alarms.
Notifies users quickly by short messages, phone calls, emails, and sound and light.
Alarm settings
Sets alarm rules in advance. When a monitored object meets conditions, an alarm is generated.

## Slide 19: Monitoring Functions — Linkage Control and Security Management
Monitoring functions
Video management
Access control management
Supports the video management system and allows users to view real-time videos and historical videos of a data center, performing visualized management of video cameras.
Allows users to create, configure, and manage access rights.
Implements rights-based management for user groups.
Monitors access control events.
Processes, queries, and reports historical access control data.
Linkage control
Performs linkage control on non-core equipment based on predefined linkage policies to respond to data center O&M requirements.
Security protection management
Notes: Typical linkage control cases include air conditioner teamwork control for energy saving in data centers, video and alarm linkage for unauthorized access, and video and door opening linkage for fire. Control processes involve single event policies, calculation of multiple event indicators, and linkage policies.
Access control rights are involved in user management, permission group management, and access control management. Various events can be monitored.
Processing layer equipment are the core equipment of the monitoring system, including embedded servers, industrial control computers, and various servers with strong performance.

## Slide 20: Management Functions
The objective of data center operation management is to achieve high availability of the data center with low operation costs. To achieve this goal, the monitoring management system must have the following functions: energy efficiency management, asset management, capacity management, and O&M management.
Management functions
Asset management
Capacity management
O&M management
Uses electronic label technology to collect statistics on locations and quantities of power distribution equipment, air conditioners, and monitoring equipment in real time to improve asset stocktaking efficiency.
Collects space, power, and cooling data of a data center, analyzes capacity changes, and uses the data as the basis for user capacity planning.
Provides functions such as periodic maintenance, periodic inspection, and event (fault) management. The failure rate and duration can be reduced through accident prevention management and process-based management.
Energy efficiency
management
Calculates the power usage effectiveness (PUE) of a data center, implements visualized monitoring of the PUE, and displays the composition and changes of energy consumption.
Notes: Asset life cycle management: It is a routine basic management of IT managers in a data center. Asset management includes warehousing and distributing, placing and removing from data centers, pickup and return, repair, stocktaking, and scrapping of IT assets.
O&M management is the management of O&M before and after data center infrastructure failures occur. It is a basic management function that improves the availability of infrastructure.

## Slide 21: System Functions
The system provides common functions for each module of the monitoring management system, including user management, log management, system maintenance, and data backup.
System functions
Log management
System maintenance
Data backup
Records all operations of the monitoring management system, traces accidents, and retrieves log information.
Performs maintenance such as upgrading a system online.
Provides hot standby to back up and restore data of the monitoring system.
User management
Manages users in the system according to permission groups.
Multiple user authentication modes should be supported to ensure system security.

## Slide 22: General Control Center (1)
The general control center is an important entry for O&M management driver information. It provides the service desk and display functions and works with the O&M management system to ensure the availability of data centers.
General
control center
Service desk functions
On-duty personnel in the general control center receive system exception information from users through the service desk, making up for the omission of abnormal runtime information caused by insufficient monitoring systems.
After the on-duty personnel obtain exception information, they register and distribute service requests in the system, track the service process and quality, and review the issues to ensure that the O&M work is completed as required.
Display functions
Provides functions such as data center planning, large-screen display, 3D display, monitoring management reports, and web or mobile terminals to intuitively display the running status of a data center, improving the readability of system data.

## Slide 23: General Control Center (2)
Display
functions
Temperature map
Report management
Large-screen display
Displays the overall temperature distribution of a data center. Quickly eliminates hot spots in a data center to ensure normal operation of IT equipment, and accurately detects refrigerant leakage to prevent equipment failures and ensure security.
Collects statistics on and analyzes historical device running data and alarm events, and displays them in charts. It provides intuitive and reliable basis for data center management and decision-making.
Displays monitoring views, alarms, energy efficiency analysis, capacity, and key battery information service segments on a large screen.
3D display
Displays the data center panorama in a 3D view, showing equipment layout, alarm information, and running status to improve user experience of visualization.
Web/Mobile terminals
The monitoring system provides access management for web terminals and mobile terminal apps, which allows users to view alarms, performance, energy consumption, and resource data of a data center.
Data center planning
Users can use various graphical elements, such as curves, pipelines, and cabinets, to simulate the actual layout of a data center.

## Slide 24
Overview of the Monitoring System
Introduction to Main Functions
Introduction to Huawei Monitoring System

## Slide 25: Huawei Monitoring Management System
Huawei monitoring management system covers power monitoring, environment monitoring, and security monitoring, provides real-time status of devices inside micro-modules, alarm information, and configuration information for management, and provides visual interfaces.
-Pro

## Slide 26: Functions of Huawei Intelligent Monitoring System
Remote control: skylight
Remote sensing: temperature, humidity, smoke, and infrared
Access control device
WiFi hotspot
Micro-module PUE
iCooling intelligent group control
Access management
Battery monitoring
Mobile APP
PAD APP
POE bus
Dual power inputs
POE/wireless communication dual-route backup

## Slide 27
(Short Answer Question)What are the differences between 2-level architecture and multi-level architecture for centralized monitoring?
(Short Answer Question)What are the main functions of the monitoring system?
Notes: Answers for reference:
1. In a two-layer architecture, there is only one NMS software. In a multi-layer architecture, the NMS software is classified into upper-layer and lower-layer NMS software.
2. Monitoring functions, management functions, system functions, general control center.

## Slide 28
Overview of the Monitoring System
Introduction to Main Functions
Introduction to Huawei Monitoring System

## Slide 29
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 31
V2.0
Qian Hui
2016.5
Li Shaofeng/00486775
New
Wang Pulin/wx763618
2020.12
Li Shaofeng/00486775
Update