## Slide 1: Introduction to Other Systems of Data Center Facility

## Slide 2
In addition to the power distribution system, cooling system, and monitoring system, the data center facility has many other indispensable systems.

## Slide 3
On completion of this course, you will be able to:
  Understand systems of fire protection, fresh air, lightning protection and grounding, and integrated cabling in the data center infrastructure;
  Understand working principles and main components of these systems.

## Slide 4
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 5: Fire Extinguishing System Overview (1)
Functions:
  Fire extinguishing system automatically detects the smoke or hot air produced when a fire happens in the fire detection area, generates audible and visual alarms, and controls the automatic fire extinguishing system. In addition, the fire extinguishing system is associated with the output contacts of other devices, to control emergency lighting, evacuation signs, emergency broadcast/communication, and fire extinguishing water supply/smoke control facilities. This enables automatic monitoring, alarms, and fire extinguishing.
  Classification:
  Water fire extinguishing system: water is the most common extinguishing agent, because it is cheap and provides high extinguishing performance. Application scenarios: civil and industrial buildings.
  Foam fire extinguishing system: the foam extinguishing agent is mixed with water based on a specific proportion, and generates extinguishing foam by using a foam generating device. Application scenarios: petrochemical enterprises, oil depots, underground engineering, various warehouses, large hangars and ships.
Notes: Water fire extinguishing system: Water is the most common extinguishing agent, because it is cheap and provides high extinguishing performance. The fire extinguishing principle is that water cools and penetrates a burning object to extinguishing the fire:
  Fire hydrant water supply system: indoor and outdoor fire hydrant systems
  Closed automatic water jetting system: Closed nozzles are used. When a fire happens, the temperature rises, and the glass bead of a nozzle breaks or the fusible metal drops, enabling automatic water jetting. The system applies to buildings where the indoor temperature ranges from 4°C to 70°C.
  Pre-action water jetting system: The pipe of the system is charged with pressurized or non-pressurized gas during normal operating, without water. When a fire happens, the fire detection system opens the pre-action valve, water is injected into the pipe, and then the closed nozzle ejects water to extinguish the fire. The system applies to buildings where the indoor temperature is below 4℃ or above 70℃.
  Automatic drench water jetting system: Open nozzles are used. When a fire happens, all nozzles eject water at the same time to extinguish the fire. The system applies to high-risk buildings.
Foam fire extinguishing system:
  Stationary foam fire extinguishing system: The system consists of the stationary foam liquid fire pump, foam liquid cylinder, proportioner, foam liquid transport pipe, and foam generating device. When a fire happens, the fire pump is started and related valves are opened to enable fire extinguishing.
  Semi-stationary foam fire extinguishing system: Some devices are stationary and can be started in time. Others are non-stationary and are carried to the site when a fire happens, to work with the stationary devices for fire extinguishing.
  Mobile foam fire extinguishing system: The system generally consists of the water source (outdoor fire hydrant, fire pool, or natural water source), foam fire fighting truck or foam generating device, water band, foam gun, and proportioner. When a fire happens, all mobile facilities are carried to the site and form a fire extinguishing system based on connection of pipes and water bands.

## Slide 6: Fire Extinguishing System Overview (2)
Classification:
  Gas fire extinguishing system:
    The extinguishing agent is stored in a pressure vessel in a liquid, liquefied gas, or gas state. During fire extinguishing, the extinguishing agent is sprayed in a gas (steam or mist) state.
    The gas fire extinguishing system is mainly applied to places with valuable equipment or places where water fire extinguishing is not applicable. Such places and equipment include telecom equipment rooms, radio and television equipment, generator rooms, electrical equipment rooms, transformers, oil circuit breakers, motors, internal combustion engines, electric locomotives, library and archive buildings, scientific experiment buildings, valuable equipment rooms, large ships, and oil product factories.

## Slide 7: Structure of the Fire Extinguishing System (1)
The fire extinguishing system consists of the automatic fire alarm system, gas fire extinguishing system, smoke control system, safety evacuation system.
  Automatic fire alarm system: in the early stage of fire, the system converts the physical signals, such as smoke, heat, and flame produced by fire, to electrical signals through the fire detector, and transmits them to the fire alarm controller to trigger relevant linkages so that people may detect the fire and take effective measures in a timely manner.
  Gas fire extinguishing system: The system stores extinguishant in the form of liquid, liquefied gas, or gas in a pressure vessel, and releases the extinguishant in the form of gas to extinguish a fire. The extinguishant diffuses evenly in a protected zone with a regulatory concentration sufficient to put out a fire from all directions.
  Smoke control system: The system exhausts the large amount of smoke produced by fire and prevents the smoke diffusing out of the protected zone to ensure the smooth evacuation and sheltering of people in the building and create favorable conditions for firefighters to put out the fire.
  Safety evacuation system: The system disconnects the non-firefighting power supplies in the case of fire and maintains proper lighting in the evacuation route and other necessary places to facilitate personnel evacuation and accident handling.

## Slide 8: Structure of the Fire Extinguishing System (2)
Automatic fire alarm system
Fire extinguishing system
Smoke control
Safety evacuation
Firefighting system
Ventilation
HVAC
Cooling
Humidifying
Fresh air
Medium- and high-voltage power distribution
Power supply system
Low-voltage power distribution
Backup power source
Transformer
UPS
Access control
Integration management
CCTV
Power and environment monitoring
Power supply
Linkage
Linkage
Linkage
Linkage control
Linkage control
Linkage control

## Slide 9: Structure of the Automatic Alarm System
Monitoring platform
Fire power supply
Network adapter
Network components
VESDA
Air sampling pipe
Smoke detector
Heat detector
Manual fire alarm button
Audible and visual alarm
Alarm bell
Fire alarm controller
I
Network adapter
Gas fire extinguishing controller
Gas fire extinguishing system
Fire display panel
I/O
I/O
Fire broadcast
Fire telephone
Backup power supply
I/O
O
O
Smoke control system
Safety evacuation system
Others
Electromagnetic valve and pressure switch
Smoke exhaust device, air supply device, fresh air device, and ventilation device
Fire pump and non-fire power supply
Emergency lighting and evacuation indication
Emergency start/abort switch, gas release indicator, and audible and visual alarm
Very early alarm control system
Notes: The automatic alarm system consists of the VESDA, air sampling pipe, fire alarm controller, smoke detector, heat detector, manual fire alarm button, audible and visual alarm, alarm bell, fire display panel, power supply, control module, fire telephone, fire broadcast, and gas fire extinguishing controller.

## Slide 10: Automatic Fire Alarm System (1)
Components | Picture | Description
VESDA |  | VESDA is short for very early smoke detection apparatus. Work principle: Sampling pipes distributed in the protected areas collect air samples. A special device filters out the dust in the air samples and transfers the air samples to the laser detection compartment. The laser detection compartment detects smoke particles in the air caused by burning, determines whether a fire happens by using a program, and generates an alarm as required.
Air Sampling Pipe |  | The air sampling pipe collects air samples for the VESDA. Sampling holes are evenly distributed on the pipe.

## Slide 11: Automatic Fire Alarm System (2)
Components | Picture | Description
Smoke Detector |  | The smoke detector is a fire detector that detects smoke particles caused by burning. Two types of smoke detectors are available: spot-type smoke detectors and line-type smoke detectors. The transmitter and receiver of a spot-type smoke detector are configured on the same device, and those of a line-type smoke detector are separated. Therefore, spot-type smoke detectors are preferred in small space (with a floor height of less than 9 m).
Heat Detector |  | The heat detector detects the ambient temperature based on the temperature sensitivity of thermosensitive components. It is generally used with the smoke detector and especially applicable to places with significant temperature rise in a fire. Spot-type and line-type heat detectors are available.

## Slide 12: Automatic Fire Alarm System (3)
Components | Picture | Description
Manual Fire Alarm Button |  | The manual fire alarm button is installed in a public place. When confirming that a fire happens, staff can push down the organic glass sheet on the button, to send a fire alarm signal to the fire alarm controller. After receiving the alarm signal, the fire alarm controller displays the ID or location of the alarm button and generates an audible alarm. Such an alarm is more emergent than a detector alarm and generally requires confirmation.
Audible and Visual Alarm |  | The audible and visual alarm is installed onsite and is enabled by the fire alarm controller. After being enabled, the alarm generates strong audible and visual alarms to remind onsite personnel.

## Slide 13: Automatic Fire Alarm System (4)
Components | Picture | Description
Alarm Bell |  | Similar to the audible and visual alarm, the alarm bell generates fire alarms that are differentiated from the ambient sound and light, to remind onsite personnel to perform safety evacuation and fire extinguishing.
Fire Display Panel |  | The fire display panel is a fire alarm display device designed by using a single-chip microcomputer, and is installed on a building floor or in an independent fire protection area. Digit-based and text-based fire display panels are available. The fire display panel is connected to the fire alarm controller through a bus, and processes and displays the data received from the fire alarm controller.

## Slide 14: Automatic Fire Alarm System (5)
Components | Picture | Description
Control Module |  | The fire control module, also called an I/O module, is an important component of the fire linkage control system, and is connected to external devices in the automatic fire alarm system, such as smoke valves, air supply valves, and fire valves.
Fire Telephone |  | The fire telephone is used for communication between the fire control center and the site. It enables multi-party calls and can be used to report alarms, check fire information, arrange for rescue, and exchange fault information. Generally, the fire telephone consists of a main phone set and extension telephones.

## Slide 15: Automatic Fire Alarm System (6)
Components | Picture | Description
Fire Broadcast |  | The fire broadcast is used by the fire control center to evacuate personnel. Generally, the fire broadcast consists of the emergency broadcast controller, power amplifier, and sound box.
Gas Fire Extinguishing Controller |  | The gas fire extinguishing controller automatically controls the start/stop of the gas fire extinguishing system. It can be connected to the emergency start/abort switch, manual and automatic transfer switches, gas release indicator, and audible and visual alarm. In addition, the gas fire extinguishing controller provides electromagnetic valve driving interfaces, to enable gas fire extinguishers.

## Slide 16: Automatic Fire Alarm System (7)
Components | Picture | Description
Fire Alarm Controller |  | The fire alarm controller is the core of the automatic fire alarm control system. It receives detection signals, processes alarm information, and provides a linkage alarm platform. Based on the structure, fire alarm controllers are classified into the wall-mounted, cabinet, and table types. A wall-mounted fire alarm controller contains a maximum of two loops and connects a small number of alarm points. A cabinet-type or table-type fire alarm controller contains more loops, has a large capacity, and provides bus and multiline linkage control, meeting the requirements of the complex fire alarm and linkage control system.

## Slide 17: Structure of the Gas Fire Extinguishing System
Fire
Fire alarm
controller
Visual inspection
Manual operation on the panel
Onsite manual operation
Mechanical emergency start/abort
Gas fire extinguishing controller
Alarm bell
Audible and visual alarm
Gas release indicator
Other linkage
Pressure annunciator
Start device
Fire cylinder (with the extinguishing agent)
Fire pipeline
Nozzle
Smoke exhaust device
Gas fire extinguishing system
Notes: The gas fire extinguishing subsystem consists of the fire cylinder (containing the extinguishing agent, extinguishing agent vessel, and vessel valve), start device (start vessel or electromagnetic valve), fire pipeline, nozzle, pressure annunciator, and other auxiliary devices. The auxiliary devices include the fire cylinder rack, high pressure hose, one-way valve for the extinguishing agent, manifold, start cylinder rack, start pipeline, one-way valve for air flows, selector valve, flange joint, and safety valve.

## Slide 18: Heptafluoropropane Extinguishing Agent
Heptafluoropropane is an environment-friendly extinguishing agent well recognized around the world. It causes no damage to the ozone layer and has the following advantages: superb fire extinguishing performance, no pollution, no conductivity, small storage space, low operating pressure of pipelines, and no slag after fire extinguishing. The extinguishing agent is stored in a liquid state and released as gas. After discharge, the gas is naturally released or fast released based on a ventilation system. No slag is left onsite.

## Slide 19: Gas Fire Extinguishing System (1)
Components | Picture | Description
Fire Cylinder |  | The fire cylinder consists of the extinguishing agent vessel and vessel valve. The extinguishing agent vessel is generally a red steel seamless container covered with epoxy painting, and can be recharged with the extinguishing agent. The extinguishing agent is stored in the vessel in a liquid state and is pressurized to the operating pressure by using nitrogen. When a fire happens, control air flows from the start cylinder trigger an action of the pneumatic valve. Therefore, the vessel valve is opened to release the extinguishing agent. When an emergency occurs, staff can remove the manual safety pin and press the manual button. The vessel valve is immediately opened.
Start Device |  | The start device stores startup gas (high-pressure nitrogen) and can be started electrically or manually. It releases startup gas to open the selector valve and vessel valve and provides the following functions: sealed storage, release, recharge, low-pressure discharge, and pressure display.

## Slide 20: Gas Fire Extinguishing System (1)
Components | Picture | Description
Fire Pipeline |  | The fire pipeline transports the extinguishing agent to the terminal nozzle. Generally, main pipelines and branch pipelines are available, with different diameters. The pipeline diameter is designed based on the extinguishing agent flow rate.
Nozzle |  | The nozzle ejects the extinguishing agent in a specific jet form. Therefore, the extinguishing agent is quickly vaporized and reaches the extinguishing concentration in the protected space. Generally, seam-type, pipe mouth-type, and atomizer nozzles are available.

## Slide 21: Structure of the Smoke Control System
Fire detector
Other linkage
Fire alarm controller
I/O
Hang wall
Manual emergency startup button
(Optional) Partition wall
I/O
Start
Smoke vent (smoke valve)
Start linkage
Smoke exhaust fan
Smoke duct
Smoke exhaust
fire valve
Automatically closed at 280C
Manual emergency startup button
Manual emergency startup button
I/O
I/O
Automatic smoke exhaust window
Manual emergency startup button
or manual smoke exhaust window
I/O
Pressurization air supply vent
Start linkage
Pressurization air supply fan
Air supply duct
Manual emergency startup button
Manual emergency startup button
I/O
Start
Either-or
Fresh air units of air conditioners
Smoke control system
Notes: The smoke control subsystem consists of the pressurization air supply fan, pressurization air supply vent, air supply duct, smoke exhaust fan, smoke vent (smoke valve), smoke exhaust fire valve, smoke duct, and auxiliary materials. The auxiliary materials include the hang wall (optional), automatic smoke exhaust window (optional), manual emergency startup button, pipe hangers and supports, power cables, signal cables, and control modules (I/O modules and input modules).

## Slide 22: Smoke Control System (1)
Components | Picture | Description
Pressurization Air Supply Fan |  | The pressurization air supply fan mechanically supplies air to staircases, elevator lobbies, and other protected areas, to generate positive pressure in the areas and prevent smoke from entering the areas. This ensures personal safety during evacuation. The pressurization air supply fan is generally selected based on parameters such as the air capacity, atmospheric pressure, power, and noise.
Pressurization Air Supply Vent |  | The pressurization air supply vent is also called a positive-pressure air supply vent or a multi-leaf air supply vent. An aluminum alloy air vent is installed in the front of the valve body. The valve body is generally installed on the side wall of an elevator lobby or a staircase. A handling cell is set near the valve body and is configured with a movable door to facilitate operations.

## Slide 23: Smoke Control System (2)
Components | Picture | Description
Air Duct |  | The air duct supplies air or exhausts smoke. The cut-off surface of the air duct is a rectangle or circle. Common air duct materials include thin steel plates, plastic, plywood, fiberboards, concrete, concrete and reinforcing steel, bricks, asbestos cement, and slag gypsum boards.
Smoke Exhaust Fan |  | The smoke exhaust fan exhausts smoke out of a building, to remove smoke, improve the visibility in the building, and facilitate fire extinguishing. The smoke exhaust fan is generally selected based on parameters such as the air capacity, atmospheric pressure, power, and noise.
Smoke Vent |  | The smoke vent, also called a smoke valve, is installed on a pipeline of the smoke exhaust system. It is normally closed during proper operating and is opened upon a fire to exhaust smoke.

## Slide 24: Structure of the Safety Evacuation System
Automatic fire alarm controller
Manual alarm button
Fire detector
Other linkage
Power distribution device for emergency lighting
Fire emergency lights
Emergency lighting controller
Centralized power supply for emergency lighting
Power supply/distribution system
Fire evacuation indicators
Notes: The safety evacuation design applies inside data centers and contains two parts: emergency lighting and safety evacuation.
The safety evacuation system consists of the fire emergency lights, fire evacuation indicators, emergency lighting controller, power distribution device for emergency lighting (power distribution box for emergency lighting), and centralized power supply for emergency lighting.

## Slide 25: Safety Evacuation System (1)
Components | Picture | Description
Fire Emergency Light |  | The fire emergency lights provide lighting for personnel evacuation and fire extinguishing. Key parameters include the input voltage, luminous flux, light source type, and power.
Fire Evacuation Indicators |  | The fire evacuation indicators provide the following functions by using signs or text: Indicate the exit, current floor, and shelter floor (room); Indicate the evacuation direction; Indicate the locations and directions to the fire extinguishers, fire hydrant boxes, fire lifts, and stairs for the disabled; Indicate the blocked passages and places and the storage locations of hazardous materials.

## Slide 26: Safety Evacuation System (2)
Components | Picture | Description
Emergency Lighting Controller |  | The emergency lighting controller controls and displays the operating status of the following components: fire emergency lights, centralized power supply for emergency lighting, power distribution device for emergency lighting (power distribution box for emergency lighting), and other accessories.
Power Distribution Device for Emergency Lighting |  | The power distribution device distributes power for the emergency lighting and evacuation indication system. Key parameters include the input voltage, output voltage, capacity, and operating time upon power failure.
Centralized Power Supply for Emergency Lighting |  | When a fire happens, the centralized power supply provides power for the fire emergency lights based on batteries. Key parameters include the power capacity, output voltage, and backup time.

## Slide 27
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 28: Fresh Air System Overview
A fresh air system refers to delivering the filtered outdoor fresh air indoors and exhausting the indoor stale air outdoors, achieving system balance while exchanging the air. This system makes scientific convection in a closed environment possible.
Functions:
  Maintain the positive pressure difference between the data center and the outside and avoid the entry of dust, ensuring better cleanliness; provide the data center with adequate fresh air, creating a favorable working condition for the personnel; treat the outdoor contaminated air, ensuring the safety of devices inside.

## Slide 29: Composition of the Fresh Air System
The fresh air system consists of the fresh air unit (fan, filter, humidifier, pre-cooling and heat reclamation devices), air exhaust pipes, and air exhaust vents. Out of these, the exhaust fan and filter are mandatory for the fresh air unit. The humidifier, pre-cooling and heat reclamation devices, and chemical filter are optional modules.

## Slide 30: Functions of the Components (1)
Fan
    Fans include the air supply fan and exhaust fan. They are the mandatory items for the fresh air system. They can be variable-frequency and constant-frequency. In general, you are advised to configure a differential pressure controller and select the variable-frequency ones.
Filter
    Filters include the coarse-efficiency filter and medium-efficiency filter. The former is a plate filter and the latter is a bag filter. In general, the coarse-efficiency filter is G3 or G4, and the medium-efficiency filter is F5 to F8 in filtering level. The configuration principle of these two types of filters is that the difference should not be greater than four levels. The higher the filtering level, the higher the filtering efficiency, and the higher the cost. Figures on the right show a coarse-efficiency filter and a medium-efficiency filter respectively.

## Slide 31: Functions of the Components (2)
Pre-cooling/Dehumidification device
  When the fresh air is not delivered to the air return vent of the indoor air conditioner (the indoor air conditioner bears the fresh air loads), you need to configure a pre-cooling section to meet the air supply requirements.
  When the humidity control uses the independent fresh air control, and the outdoor humidity is higher than the indoor control target, you need to configure a dehumidification section (the cooling dehumidification is generally adopted).

## Slide 32: Functions of the Components (3)
  Humidifier
  When the humidity control uses the independent fresh air control, and the outdoor humidity is lower than the indoor control target, you need to configure a humidification section.
Wet film humidifier
Infrared humidifier
High-pressure micro-mist humidifier
Electrode
Electrode humidifier

## Slide 33: Functions of the Components (4)
  Heat reclamation device
    To save energy, you can configure a heat reclamation section, using exhaust air to preheat or pre-cool the fresh air. There are two working modes, namely plate type and rotary-wheel type. The figure on the right shows the rotary-wheel heat reclamation.
  Heater
    You need to configure the heating section only when the fresh air unit adopts the constant-temperature and constant-humidity air supply solution.
    After the cooling and dehumidification, heat the fresh air unit to dry bulb working conditions at the air supply vent. This solution is not energy-saving and therefore is not recommended.

## Slide 34
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 35: Cabinet Overview
Standard cabinets are widely used in stacking the integrated cabling and cable distribution equipment, computer network equipment, communications equipment, and electronic equipment. Cabinets are classified into server cabinets, network cabinets, and console cabinets.
Cabinets provide the enhanced electromagnetic shielding, reduce the equipment operating noise, and lower the footprint. Some high-end cabinets have the air filtering function, which improves the operating environment for precision equipment.
Simple in structure, standard cabinets mainly include the basic framework, internal supporting system, cabling system, and ventilation system.
General specifications of cabinets are 600 mm or 800 mm in length, 600 mm, 800 mm, or 1000 mm in width, and 24 U, 36 U, 42 U, or 47 U in height.
Notes: The installation heights of devices in a 19-inch standard cabinet are represented by a special unit, U, which is 44.45 mm.

## Slide 36: How to Select a Cabinet?
Load-bearing performance: The cabinet must be solid enough to bear the increasingly small-sized, network-based, rack-mounted, and large-capacity heavy IT devices.
Temperature control: The cabinet must have sufficient heat dissipation capabilities.
Cable management: The cabinet must provide sufficient cable channel and support top and bottom cable routing. The cables must be laid out conveniently and orderly. The cabinet must be close to the cable ports to shorten the cable routing distance and reduce the space occupied by the cables.
Power distribution management: The cabinet must support the vertical installation of a dedicated PDU with two inputs without affecting installation, use, or maintenance of devices. The PDU is often equipped with SPDs.
Protection performance: The cabinet door stile and frame must be reliably grounded. Inside the cabinet there are ground points. The working ground bar and protection ground bar can be connected to the grounding copper bar of the data center. The cabinet is equipped with various monitoring devices for monitoring the temperature, humidity, voltage, current, and smoke.
Notes: Rack-mounted IT devices in the data center bring some changes in cabinet specifications, mostly represented by the increasingly smaller volume of single servers. Servers occupy an increasingly smaller height space and larger depth space, meaning lifting requirements for cabinet depth.
The cabinet must have the cycle channel for cold and hot air exchanging to avoid that the air inside the cabinet is either too hot or too cold for the products, ensuring efficient running of IT devices.
Cable management: Ensure that the heat dissipation airflow will not be blocked by the cables, and that the fault can be quickly located if somewhere in the device cable layout is faulty.
Power distribution management: The design for the cabinet power distribution system should take the reliability design as the core and special cabinet design, well coordination, and seamless cooperation with other systems as the principles. In addition, installation convenience, intelligent management, adaptation, and simple O&M should also be considered.

## Slide 37
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 38: Lightning Overview
Lightning phenomenon: Lightning is a result of mutual high-speed movements and fierce friction between clouds in the sky, causing the high-end clouds and low-end clouds to be with opposite charge. In the meantime, the low-end clouds also induce a large amount of hetero-charges on the ground to form a tremendous capacitance. When the capacitive field reaches a certain threshold, the ground discharge is generated.
Lightning hazards
  The thermal effects of the lightning current can blow the conducting wires and burn out the electrical equipment.
  The electrodynamic force generated by the mechanical effects of the lightning current can smash the equipment, towers, and buildings, as well as cause injuries to people and livestock.
  The electromagnetic effects of the lightning current can generate overvoltage, break down insulated electrical equipment, and even cause fire and explosion, which may hurt and kill people.

## Slide 39: Basic Forms of Lightning Overvoltage
Direct lightning strike: The lightning strikes the electrical devices, cable routes, buildings, and other objects.
Induction lightning strike: Overvoltage is caused by electrostatic induction or electromagnetic induction from the lightning to the cable routes, devices, or other objects.
Induced overvoltage on the overhead cable routes

## Slide 40: Lightning Arrester
The lightning arrester consists of three parts: air-terminal system, downlead, and grounding device.
  Air-terminal system (lightning receiver): It is a metal conductor that receives the lightning current, and normally uses the lightning rod, lightning conductor, or lightning net (belt).
  Downlead: Ensure that the lightning current does not melt the downlead. Generally, the downlead is made of steel tube whose diameter is at least 10 mm or flat steel whose cross-sectional area is at least 80 mm2.
  Grounding device: It is a general term for ground conductors and earthing electrodes buried under ground.
Notes: Lightning rod.

## Slide 41: Grounding Overview
Grounding refers to connecting certain parts of the electrical equipment or certain points of the power system to the ground to provide a pathway for discharging the faulty current or lightning current, stabilize potential, and provide the zero potential reference point. It ensures the safe operation of the power system and electrical equipment, as well as personal safety.
The grounding function is implemented by the grounding device or grounding system.

## Slide 42
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 43: Integrated Cabling System Overview
An integrated cabling system is the information transmission channel inside a building or between buildings. It connects voice equipment, data equipment, message exchange equipment, and building automation management equipment in a building to provide a unified physical transmission medium for the building. At the same time, it connects information communications equipment in the building to an external communications network.
Features:
  It is a modular and highly flexible information transmission system inside a building or between buildings.
  Its equipment is independent of lines and features flexibility, openness, compatibility, reliability, economy, and advancement.
  It adopts unified design and planning for voice and data signals. Unified transmission lines and information connectors are used to transmit different signals in a standard cabling system.

## Slide 44: Composition of the Integrated Cabling System
The Integrated Cabling System is composed of six subsystems: work area subsystem, horizontal subsystem, backbone subsystem, management subsystem, equipment room subsystem, and campus subsystem.

## Slide 45: Integrated Cabling in Data Centers
The determination of cabling mode is an important step of the data center planning. Ignoring the cabling mode reflects the blindness and confusion of the data center planning.
Cabling modes are classified into overhead cabling and underfloor cabling:
  Overhead cabling: cables laid out in spaces higher than the device height;
  Underfloor cabling: cables routed under the raised floor;
  Cabling on the top of cabinets: troughs for data cables and power cables installed on the top of each cabinet to route cables to each cabinet.
Notes: Compared with the underfloor cabling, the overhead cabling is a little complicated. This layout generally applies to standard rack-mounted scenarios. Consistent dimensions, especially consistent height, make an appealing appearance. In addition, the overhead cabling usually uses the cable trough or cable tray to support the cables. Cable troughs and cable trays can be further classified into different materials and installation modes. These are the factors that need to be considered in design and planning.

## Slide 46
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 47: Composition of Indoor Decoration System
Electrostatic discharge (ESD) raised floor decoration: As the floor is removable, cable connections, pipe connections, and maintenance are convenient.
Ceiling decoration: The area above the suspended ceiling is used as the plenum space for air supply or return in a data center, where ventilating ducts can be deployed.
Partition decoration: mainly includes partition walls and wall decoration. It requires sound insulation, thermal insulation, and fire prevention.
Shielding system: It is mainly used for anti-interference and information confidentiality. It not only prevents indoor information from leaking or being detected through electromagnetic waves, but also prevents external electromagnetic interference. Common use cases of shielding systems include rooms shielded with metal mesh or plate and shielded cabinets.
ESD floor
Suspended ceiling and partition
Shielded room
Notes: Acceptance items of the indoor decoration engineering include the decoration of suspended ceilings, partition walls, doors, windows, walls, the acceptance of floors and raised floors, and other indoor operations. All indoor decoration operations and construction should comply with corresponding specifications and standards.
Decoration of ESD floors: The ideal height of a raised floor ranges from 18 to 24 inches (46 to 61 cm). The floor of a building should meet design requirements and be clean and dry. When the raised floor space is used as a plenum, the walls and floor should be dust-proof and should not be peeled or cracked. Take protective measures for raised floors when moving or installing equipment on them. After laying out ESD floors, ground them properly.
The surface of the suspended ceiling in a computer room should be flat and free from dust, discoloration, and corrosion. Edges should be neat without warping. After edges are sealed, the adhesive should not be peeled off. Thermal insulation and sound insulation materials used for filling the ceiling should be flat and dry, and seams should be wrapped.
Waveguide window: prevents electromagnetic waves from passing through but allows air to flow through.
Power filter: Each power cable entering shielded rooms must be configured with a power filter.

## Slide 48
(Short Answer Question) Which kind of fire extinguishing system is applied to data centers?
(Short Answer Question) Why is overhead cabling more popular?
Notes: Answer 1: Gas fire extinguishing system (heptafluropropane).
Answer 2:
  Underfloor cabling is easy to implement and cost-effective. Overhead cabling poses great pressure on the cable tray when the cable density and capacity are high.
  The popularity of overhead cabling in recent years is closely related to the continuous upgrading of the data center scale, the popularity of downflow cooling, and the importance attached to maintenance management by customers. By contrast, the underfloor cabling is prone to some fatal defects, such as non-rodent-proofing, massive dust, difficult maintenance, and inconvenient fire extinguishing. Besides, data center projects in China nowadays are restricted by the floor height in the building. Underfloor cabling requires more net height than overhead cabling. Underfloor cabling also lacks flexibility in the plan layout of data centers and in coping with changes in the future.
  In fact, there are specific description about the cabling implementation requirements in provincial data center and cabling engineering technical specifications documents. Strong-current and weak-current cables in the data center should be routed separately to avoid electromagnetic interference. In general, strong-current cables need to be routed under the floor, and weak-current need to be routed overhead; strong-current cables use cable troughs, and weak-current cables use metal hoisting hangers.

## Slide 49
Fire Protection System
Fresh Air System
Cabinet System
Lightning Protection and Grounding System
Integrated Cabling System
Indoor Decoration System

## Slide 50
Huawei - Building A Better Connected World
  Huawei Enterprise：http://support.huawei.com/enterprise/
  Online Learning：http://learning.huawei.com/en/
Popular Tools
  HedEx Lite
Support Web
Enterprise APP
Support APP

## Slide 52
Course code
HCIA-DCF
V1.0
Wwx277162
2017.01.20
Li Shaofeng/l00486775
New
Wang Cong/wx760444
2020.4
Update
Li Shaofeng/l00486775