Huawei DCF Certification Training

Cooling System Load Calculation and Configuration Solution

ISSUE:2.0

HUAWEI TECHNOLOGIES CO., LTD.

Copyright © Huawei Technologies Co., Ltd. 2020. All rights reserved. No part of this document may be reproduced or transmitted in any form or by any means without prior written consent of Huawei Technologies Co., Ltd. Trademarks and Permissions and other Huawei trademarks are trademarks of Huawei Technologies Co., Ltd. All other trademarks and trade names mentioned in this document are the property of their respective holders. Notice The purchased products, services and features are stipulated by the contract made between Huawei and the customer. All or part of the products, services and features described in this document may not be within the purchase scope or the usage scope. Unless otherwise specified in the contract, all statements, information, and recommendations in this document are provided "AS IS" without warranties, guarantees or representations of any kind, either express or implied. The information in this document is subject to change without notice. Every effort has been made in the preparation of this document to ensure accuracy of the contents, but all statements, information, and recommendations in this document do not constitute a warranty of any kind, express or implied.

| Huawei Technologies Co., Ltd. |  |
| --- | --- |
| Address: | Huawei Industrial Base Bantian, Longgang Shenzhen 518129 People's Republic of China |
| Website: | http://e.huawei.com |

Huawei Certificate System

Huawei Certification follows the "platform + ecosystem" development strategy, which is a new collaborative architecture of ICT infrastructure based on "Cloud-Pipe-Terminal". Huawei has set up a complete certification system consisting of three categories: ICT infrastructure certification, Platform and Service certification and ICT vertical certification, and grants Huawei certification the only all-range technical certification in the industry. 
    Huawei offers three levels of certification: Huawei Certified ICT Associate (HCIA), Huawei Certified ICT Professional (HCIP), and Huawei Certified ICT Expert (HCIE).

Contents

1 Data Center Cooling System Configuration	4

1.1 Data Center Cooling System Requirements	4

1.1.1 Description of a Data Center Cooling System	4

2 Training	5

2.1 Training Description	5

2.1.1 About This Training	5

2.1.2 Training Objectives	5

2.1.3 Training Background and Requirements	5

2.1.4 Planning Methods	6

2.1.5 Planning Steps	7

2.2 Task Description	7

2.2.1 Task 1: Estimating Cooling Load of the Cooling System	7

2.2.2 Task 2: Completing the Air Conditioner Configuration Reference Table	8

2.2.3 Task 3: Determining the Configuration Solution	8

2.2.4 Task 4: Discussing and Determining a Chilled Water System	12

2.2.5 Task 5: Selecting Devices and Optimizing the Chilled Water System	13

2.2.6 Task 6: Providing Cooling System Configuration Suggestions	14

Data Center Cooling System Configuration

Data Center Cooling System Requirements

Description of a Data Center Cooling System

In most cases, precision air conditioners dedicated for data centers ensuring a constant temperature and humidity are used based on the actual conditions. With such a cooling system, a stable and good data center environment can be built.

Environment devices in data centers produce a large amount of heat and little moisture. The heat is intensively distributed. That means 95% of the heat generated by data center devices is sensible heat. The heat is large, the humidity is small; therefore the heat humidity ratio is very high. In this case, air treatment is a cooling process with constant humidity. The enthalpy difference is small. Large air volume is an inevitable choice to eliminate the residual heat.

In addition, communications devices, network devices, and servers in data centers must run uninterruptedly around the clock. Therefore, the cooling system needs to run uninterruptedly throughout the year.

Therefore, it is a common practice in the industry to calculate the cooling capacity of a data center based on the enclosure features (including the wall, ceiling, ground, floor; other factor like building direction, material of external and internal walls, door and window type, gap, and heat dissipation), personnel heat, and lighting heat, fresh air load, and heat dissipation of each device in the data center, and then determine the air conditioner capacity. The air environment parameters of a data center cooling system need to be specified based on the actual situation.

It should be noted that the data center environment is implemented by air conditioners. The following requirements must be met to ensure the cleanness of the data center:

- Seal the enclosures of data centers to keep cleanliness.

- Maintain positive pressure in data centers to avoid erosion by dirty air. Purify fresh air must by two kinds of filters, that is, primary filter and sub-high efficiency filter. In this way, the air quality of data centers will be greatly improved.

- Install medium-efficiency filters in air conditioners and replace the filters periodically to ensure continuous air purification during air circulation.

Training

Training Description

About This Training

This training aims to help trainees select appropriate air conditioner models, develop a cooling system solution, and select a layout mode and air supply mode based on the requirements of an actual project to finally determine the cooling system configuration and complete the feasibility study on the customer side.

Training Objectives

Air conditioner selection standards

Configuration calculation method

Load statistics and processing

Training Background and Requirements

The following figure shows the layout of the second floor in a data center project. Most equipment cabinets in the equipment room are 800 mm and 900 mm deep cabinets. The aisle between devices is narrow and uneven, and onsite devices are placed in disorder.

Now the original space needs to be re-planned for leasing. Based on different service requirements, three areas with high, medium, and low density are divided for deployment of different devices (blade servers, storage devices, and communication devices).

All the existing cabinets must be replaced. The replaced cabinets will be stored in the warehouse and scrapped. The reconstruction follows the principle of standardized and modular. In addition, cabinets need to be deployed as many as possible and the cooling airflow organization needs to be optimized. The limited area of the equipment room must be properly used and aisle containment is adopted to reduce energy consumption. In the high-density area, in-row cooling is recommended. In the low-density area, in-room cooling is recommended. The air conditioner configuration is designed in N+1 redundancy mode.

As the technical support of the project, Tom needs to make a feasibility study report on the cooling system to facilitate the company's decision-making.

The following figure shows the onsite layout.

The area is 7.9 m x 19.6 m. The areas of the three areas are almost the same. When reconstructing the layout, Tom needs to calculate the maximum number of IT cabinets supported in the area and finds the optimal solution through iteration in advance.

The specific layout requirements are as follows:

Cabinets are 2400 mm away from the entrance, 1200 mm away from the walls, and the distance between modules is 1200 mm.

Data center layout diagram

The total area of the data center is about 155 x 3 square meters, and the net height is about 4.5 meters.

Planning Methods

The heat load of the data center mainly comes from the heat generated by the devices and the heat load of the maintenance structure. Therefore, you need to know the quantity and power consumption of the main devices to determine the capacity and configuration of the precision air conditioners. Based on previous experience, except for heat load of main devices, other heat load, such as lighting load, maintenance structure load, supplementary fresh air load, and personnel heat load can be determined by multiplying related coefficients. The error is acceptable to customers. If accurate calculation conditions are not met, you can calculate cooling load based on equipment room area and experience.

1.	There is no complete layout plan for the data center. So the space is planned based on the module layout requirements.

2.	Calculate the number of cabinets based on the layout and calculate the cooling requirement of the cabinets with full load.

3.	Select appropriate air conditioners and meet the N+1 redundancy requirement.

Planning Steps

Calculate the maximum number of cabinets that can be supported to obtain the general range of IT loads that can be supported.

Configure the UPSs based on the IT load power. (You can choose whether to deploy the UPS in the aisle containment. It is recommended that the UPS not be deployed in the aisle containment.)

Calculate the cooling loads in different areas.

Analyze the application scenario type.

Determine the air conditioner type. (Take Huawei air conditioners as an example. Select two in-row solutions.)

Select air conditioners, develop a configuration solution, and verify whether the solution meets the requirements.

Determine the air supply modes.

Develop a feasibility study report.

Task Description

Task 1: Estimating Cooling Load of the Cooling System

Description

Subtask 1: Based on the obtained materials, estimate the possible layout solutions in the R1, R2, and R3 areas and the number of cabinets for each solution.

Subtask 2: Calculate the cooling load in the areas with different power densities based on the load calculation principle. (Do not need to consider the moisture load.)

Task execution rules:

Trainees of each group obtain the plane information description and load statistics table of the project from the trainer and read the related information.

Trainees discuss and calculate for 20 minutes, and write the calculation process and results on the electronic whiteboard. Give 1 point if the calculation task is completed, 2 points if the total load calculation range is correct, and 1 point if the cooling load indicator value is reasonable.

Each group explains the calculation process and how to select parameters.

Tip: You can use the load statistics table in the smart module layout slides.

Task 2: Completing the Air Conditioner Configuration Reference Table

Task Arrangements

Subtask 1: Discuss in group and determine the technical parameters and factors that affect the configuration of air conditioners when the total cooling load is determined.

Subtask 2: Read the recommendation table and use Huawei NetCol5000-A025/NetCol5000-A042 as an example to complete the table (derating is not considered).

| Item | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Task 3: Determining the Configuration Solution

Task description: Based on the cooling load estimation result, equipment room level requirements, and the configuration table obtained in task 2, each group develops a suitable air conditioner configuration solution and layout solution, fills in the following table (humidification and power distribution are not considered), and demonstrates the table on the stage.

Air Conditioner Selection Rules

Determine whether to use in-row or in-room air conditioners based on the cost, space, and service requirements (power density of a single cabinet).

If the power density of a single cabinet is higher than 5 kW, select in-row air conditioners. If the power density of a single cabinet is 8 kW or lower, select in-room air conditioners.

When air is supplied under floors or inside walls, select in-room air conditioners.

Generally, select air conditioners of the same type in the same area.

Rules for Determining the Number of Air Conditioners

The number of air conditioners is generally calculated by dividing the total cooling load by the cooling capacity of a single air conditioner. The number is rounded up using the RoundUp function. The cooling capacity of a single air conditioner is calculated using software based on the indoor unit temperature and humidity (23/35°C is recommended in design working conditions) and outdoor unit temperature and humidity (extreme temperature and humidity).

For example, assume that the total load is 125 kW, and the cooling capacity of a single air conditioner is 39 kW (calculated based on the software model).

RoundUp (125/39,0) = RoundUp (3.206,0) = 4

When determining the quantity of air conditioners, standby air conditioners need to be considered. If the quantity of air conditioners is less than or equal to 7, one air conditioner is added as the standby air conditioner (N+1). If the quantity of air conditioners is greater than or equal to 8, two air conditioners are added as standby air conditioners (N+2).

      - Rules for Selecting a Power Supply Solution

Air conditioners with dual power supplies (one serves as the primary supply and the other serves as the standby supply) are preferred. During power distribution, half of air conditioners use route A as the active route and route B as the standby route. The other half of air conditioners use route B as the active route and route A as the standby route. This works for both in-room air conditioners and in-row air conditioners.

If continuous cooling is required, a UPS can be deployed in addition to the preceding two routes of power supply.

Example:

      - Humidification Solution Selection Rules

In most cases, deploy two humidification (heating) air conditioners in the same area. If one air conditioner is faulty, the other air conditioner keeps working. Air conditioners are interlaced and kept a certain distance in between.

The formula for calculating the humidification capacity is as follows:

W = ρ x V x (d1 – d2) x C x 1.2

Where: ρ indicates the air density (1.2 kg/m), V indicates the dehumidification space volume m, d1 indicates the air moisture content after humidification, d2 indicates the air moisture content before humidification, and 1.2 is the safety coefficient.

For example, assume that the volume of a room is 700 m3. Before humidification is performed, the temperature is 25°C, and the relative humidity is 30% (the absolute humidity d2 is 5.983 g/kg as specified in the psychrometric chart). After humidification is performed, the temperature is 25°C, and the relative humidity is 50% (the absolute humidity d1 is 10.037 g/kg as specified in the psychrometric chart).

Humidification capacity W = ρ x V x (d1 – d2) x C x 1.2 = 1.2 x 700 x (10.037 – 5.983) x 1.2 = 4.086 kg

If the humidification capacity of a humidifier is 4.5 kg/h, two dehumidifiers are required. One active and one standby.

The following figure shows the layout of precision air conditioners with the humidification function.

      - Outdoor Unit Selection Rules

Determine whether the outdoor unit is a T1 or T3 (for areas where the ambient temperature is greater than 45°C) unit based on the local ambient temperature.

If the ambient temperature is less than –20°C, add a low-temperature component.

Select A, B, C, and D outdoor units according to local environmental classes.

      - Selection Process

Use the blue column in the following table as an example. If the total number of cabinets is 12, this column lists all possible situations in the 25 kW air-cooled scenario. You only need to select a solution as required. In other scenarios, you can obtain the final solution by making an exhaustion table like this.

Reference solution:

For a single smart module, if the total number of cabinets is 18, you can deploy 12 or 16 IT cabinets. It is recommended that you select an even number of cabinets to facilitate symmetrical installation and layout. You can also list the solutions with odd number of cabinets in the table.

For example, if 16 IT cabinets are installed, you can only deploy four Netcol5000-A25 kW air conditioners, and the power density of a single cabinet is 3 kW.

| Item | Quantity | Remarks |
| --- | --- | --- |
| Netcol5000-A25 kW | 4 | One redundancy beside the module |
| Netcol5000-A26 kW | 4 |  |
| Accessories | Xx |  |

    - Task 4: Discussing and Determining a Chilled Water System

Discuss in groups about the following questions: According to the five classification methods of chilled water system of air conditioners in intensive lectures, what factors need and need not to be considered in the feasibility study phase when a chilled water system is selected in this project? If the chilled water system shown in the slide is configured, can the system meet the fault tolerance requirement and why?

    - Task 5: Selecting Devices and Optimizing the Chilled Water System

Subtask 1: Assume that the chilled water in-row solution is selected and two chillers listed in the table are selected. Discuss in groups whether the chillers can meet the requirements.

| Device Name | Specifications | Quantity | Input Power |
| --- | --- | --- | --- |
| Centrifugal chiller | 300 RT | 2 | xxx kW |

Subtask 2: If the data center is built in a subfrigid zone and the time when the temperature is lower than 20°C accounts for more than half of a year, what methods can be used to save energy and reduce the PUE?

Subtask 3: If the customer uses the direct ventilation solution, calculate the required cooling capacity.

Task 6: Providing Cooling System Configuration Suggestions

Summary

Air conditioner configuration suggestions

Cooling source type:

Power density of a single cabinet:

Technology adopted to improve the utilization of cold air:

Pipeline deployment:

Cooling source of the air conditioner:

The following uses the high-density area as an example. The configurations of air conditioner loads and cooling sources are as follows:

| No. | Item | Air Conditioner Load |
| --- | --- | --- |
| 1 | Air conditioner load |  |
| 2 | Air conditioner configuration |  |
| 3 | Chiller configuration |  |
| Others |  |  |