## Slide 1: Cooling System Load Calculation and Configuration Solution Scenario-based Training

## Slide 2
In the preparation phase of data center construction, a feasibility study report on the cooling system is provided to help select a proper cooling system. In this phase, we need to develop a basic configuration solution of the cooling system. This training will guide you to develop a configuration solution for a data center cooling system.

## Slide 3
On completion of this course, you will be able to:
  Calculate data center cooling system loads.
  Select data center air conditioner configurations and optimize the configuration solution.
  Understand the configuration and selection principles of a chilled water system and chillers.
  Optimize a cooling system and understand its simple configurations.

## Slide 4: Trainee Grouping
Steps for grouping trainees
  Before the training, the trainer prepares the same number of cards as the trainees. Each three cards have the same number.
  Trainees draw lots and those who draw cards with the same number form a group.
  Extra trainees are assigned to a group by the trainer.
  Group members determine a group name.

## Slide 5: Floor Plan of a Data Center
Notes: The floor plan is from the planning cases of [HCIE-DCF-Design] Data Center Cooling System Planning Part 3.

## Slide 6: Background
The figure on the right shows the layout of the second floor in a data center project. Most equipment cabinets in the equipment room are 800 mm and 900 mm deep cabinets. The aisle between devices is narrow and uneven, and onsite devices are placed in disorder.
Now the original space needs to be re-planned for leasing. Based on different service requirements, three areas with high, medium, and low density are divided for deployment of different devices (blade servers, storage devices, and communication devices).
All the existing cabinets must be replaced. The replaced cabinets will be stored in the warehouse and scrapped. The reconstruction follows the principle of standardized and modular. In addition, more cabinets need to be deployed and the cooling airflow organization needs to be optimized. The limited area of the equipment room must be properly used and aisle containment is adopted to reduce energy consumption. In the high-density area, in-row cooling is recommended. In the low-density area, in-room cooling is recommended. The air conditioner configuration is designed in N+1 redundancy mode.
As the technical support of the project, Tom needs to make a feasibility study report on the cooling system to facilitate the company's decision-making.
Medium-density equipment room (R2)
High-density equipment room (R1)
Low-density equipment room (R3)
Layout of the second floor in the equipment
room of the xx project
Data center phase 1 equipment room
Network equipment room
Transmission equipment room
Data center phase 1 equipment room
Notes: As shown in the preceding figure, the customer equipment room consists of the transmission equipment room, network equipment room, and phase 1 equipment room of the data center. Most equipment cabinets in the equipment room are 800 mm and 900 mm deep cabinets, and the aisle between devices is narrow. Due to the lack of an unified deployment plan, installation personnel often deploy server cabinets, storage devices, and communication devices in the nearby idle cabinets. As a result, the layout is not neat, and the direction of hot and cold supply airflow is inconsistent with that of exhaust airflow. After re-planning, the customer's equipment room is divided into R1, R2, and R3 areas. Different services are deployed in different areas.

## Slide 7: Task 1: Estimating Cooling Load of the Cooling System
Task description
  Subtask 1: Based on the obtained materials, estimate the possible layout solutions in the R1, R2, and R3 areas and the number of cabinets for each solution.
  Subtask 2: Calculate the cooling load of the cooling system in the areas with different power densities based on the load calculation principle. (Do not need to consider the moisture load.)
Task rules
  Trainees of each group obtain the project plane information description and load statistics table from the trainer and read the related information.
  Group members discuss and calculate for 20 minutes, and write the calculation process and results on the electronic whiteboard. Give 1 point if the calculation task is completed, 2 points if the total load calculation range is correct, and 1 point if the cooling load indicator value is reasonable.
  Each group explains the calculation process and how to select parameters.
Notes: The cabinet power density varies depending on the area. Trainees can flexibly select the cabinet power density in the table. The UPS and battery cabinet can be deployed inside the aisle containment or not.

## Slide 8: Layout Requirements for the Modular Data Center
Based on the smart module layout, the following solutions are available:
Single-row scenario
Dual-row scenario
Cabinet
Aisle containment
Cabinet
Aisle containment
Cabinet

## Slide 9: Load Statistics Table of the Modular Data Center
Room Name | Number of Racks | Power Density of a Single Rack (kW) | (Optional) UPS Power (kW) | Simultaneous Coefficient (Recommended Value) | Comprehensive Coefficient (Aisle Containment or Open) | Total Cooling Capacity (kW)
High-density equipment room (R1) |  | 10 kW–20 kW |  |  |  | 
Medium-density equipment room (R2) |  | 6 kW–10 kW |  |  |  | 
Low-density equipment room (R3) |  | 3 kW–5 kW |  |  |  | 
... |  |  |  |  |  | 
... |  |  |  |  |  | 
Total cooling load (kW) |  |  |  |  |  | 

## Slide 10: Task 2: Completing the Air Conditioner Configuration Reference Table
Task description
  Subtask 1: Discuss in group and determine the technical parameters and factors that affect the configuration of air conditioners when the total cooling load is determined.
  Subtask 2: Read the recommendation table and use Huawei NetCol5000-A025/NetCol5000-A042 as an example to complete the table (derating is not considered).
Task rules
  Group members discuss the question for 20 minutes
  Write the discussion results on the electronic whiteboard after discussion. Give 2 points for each correct factor or parameter.
  Give 4 points for completing the table and 2 points for drawing a conclusion. Additional points can be given if the analysis of other models is completed.
Notes: In many projects, the devices deployed on the customer side are not planned. In this case, we can infer the cooling requirements based on the IT cabinet and planned power density. In the actual implementation phase, we can then perform forward verification. The main advantage of the bidirectional calculation is that the whole process is self-proper. The biggest challenge of this project is that the equipment room area on the customer side is fixed and the overall layout is not planned based on the IT power density requirements. It is to find the best solution in limited space. The contradiction in this case is that the power density needs to be maximized on the customer side, but the space is limited. One more equipment cabinet means one less cooling cabinet. The number of cooling cabinets is in direct proportion to the IT power density and in inverse proportion to the number of IT cabinets. We should find a balance point between the two factors.
Exhaustion and iteration is one of the ways to solve this problem and find the optimal solution.

## Slide 11: Recommended Selection Table
The cooling source of air conditioners is selected based on the cooling capacity, cooling range, customer requirements, and TCO.
Scenario | Floor Area | Power Density | Outdoor Unit Space | Outdoor Unit Height Difference | Recommended Cooling Solution | Remarks
Micro data center | ≤ 50 m2 | ≤ 7 kW | N/A | +20 m to –5 m | FusionModule800 + Rack-mounted air conditioner | 
Small and medium-sized DC | 50–500 m2 | ≥ 5 kW | Enough | +20 m to –5 m (+30 m to –8 m) | NetCol5000-A | 
 | 50–500 m2 | ≥ 5 kW | Insufficient or water chillers are available in the building. | N/A | NetCol5000-C + Purchased air-cooled chiller | 
 | 50–500 m2 | ≤ 5 kW | Enough | +20 m to –5 m (+30 m to –8 m) | NetCol5000-A | Smart module preferred, in-room air-cooled solution with downflow air supply
 | 50–500 m2 | ≤ 5 kW | Insufficient or water chillers are available in the building. | N/A | NetCol8000-C+ Purchased air-cooled chiller | 
Large data center | ≥ 500 m2 | ≥ 5 kW | N/A | N/A | NetCol5000-C + Purchased air-cooled/water-cooled chiller | 
 | ≥ 500 m2 | ≤ 5 kW | N/A | N/A | NetCol8000-C + Purchased air-cooled/water-cooled chiller | 

## Slide 12: Task 3: Determining the Configuration Solution
Task 3: Based on the cooling load estimation result, equipment room level requirements, and the configuration table obtained in task 2, each group develops a suitable air conditioner configuration solution and layout solution, fills in the following table (humidification and power distribution are not considered), and demonstrates the table on the stage.
Discussion rules
  Group members discuss and draw a simple layout diagram, read the configuration principles, and output the recommended configuration solution.
  Each group assigns a representative to present the configuration solution, and explain the basis for selection. The trainer gives 10 points if the configuration is reasonable and makes a summary.
  Output at least two different solutions and compare them in terms of layout and advantages.
  Discussion time: 30 minutes
Configuration Description | Number of Air Conditioners (Recommended: N+1) | Redundancy Description | Cabinet Usage Description
For example, NetCol5000A-42 kW full-sized air-cooled air conditioner | 4+1 | One standby for each module | 13 + 5 (13 IT cabinets and 5 air conditioner cabinets)
Notes: Use the table in task 2 to perform exhaustion and iteration to determine the optimal solution. For different air conditioners, use a table to list all possibilities and find the optimal solution on the premise that the maximum number of cabinets is met. The answer is usually in the table.

## Slide 13: Configuration Principles for Air Conditioners
Principles for selecting air conditioners
  Determine whether to use in-row or in-room air conditioners based on the cost, space, and service requirements (power density of a single cabinet).
  In-row air conditioners are recommended when the power density of a single cabinet is high (higher than 5 kW).
  When air is supplied under floors or inside walls, select in-room air conditioners.
  Generally, select air conditioners of the same type in the same area.
Principles for selecting full-sized and half-sized air conditioners
  A half-sized indoor unit's footprint is only 1/2 that of a full-sized indoor unit. When the floor area is determined, the full-sized indoor unit is preferred.

## Slide 14: Configuration Principles for Air Conditioners
Principles for determining the number of air conditioners
  The number of air conditioners is generally calculated by dividing the total cooling load by the cooling capacity of a single air conditioner. The number is rounded up using the RoundUp function.
  In the DX solution, the cooling capacity of a single air conditioner needs to be calculated using software or referring to charts based on the temperature and humidity of the indoor unit (23/35°C is the recommended working condition), outdoor unit temperature and humidity, and extreme ambient temperature and humidity.
  In the CW solution, the cooling capacity of a single air conditioner needs to be calculated using software or referring to charts based on the temperature and humidity of the air conditioner (23/35°C is the recommended working condition) and chilled water supply and return (such as high-temperature chilled water) working condition.
  For example, assume that the total load is 125 kW, and the cooling capacity of a single air conditioner is 39 kW (calculated based on the software model).
  RoundUp (125/39,0) = RoundUp (3.206,0) = 4
  When determining the number of air conditioners, backup air conditioners need to be considered. You can comply with the backup requirement of customers. If there is no requirement, configure one backup air conditioner (N+1) when there are less than or equal to seven air conditioners, and two air conditioners (N+2) when there are more than eight air conditioners.
Notes: Software link: http://3ms.huawei.com/hi/index.php?app=Group&mod=Core&act=showSectionData&id=1469723&gid=2031921

## Slide 15: Configuration Principles for Air Conditioners
Principles of configuring the power supply
  Air conditioners with dual power supplies (one serves as the primary supply and the other serves as the standby supply) are preferred. During power distribution, half of air conditioners use route A as the active route and route B as the standby route. The other half of air conditioners use route B as the active route and route A as the standby route. This works for both in-room air conditioners and in-row air conditioners.
  If continuous cooling is required, a UPS can be deployed in addition to the preceding two routes of power supply.
Dual power supply solution
Power supply solution
Route A
Route B

## Slide 16: Configuration Principles for Air Conditioners
Humidification solution selection principles
  In most cases, deploy two humidification (heating) air conditioners in the same area. If one air conditioner is faulty, the other air conditioner keeps working. Air conditioners are interlaced and kept a certain distance in between.
  Humidification capacity calculation formula: W = ρ x V x (d1 – d2) x 1.2
  where ρ indicates the air density 1.2 kg/m3, V indicates the dehumidification space volume (m3), d1 indicates the air moisture content after humidification, d2 indicates the air moisture content before humidification, and 1.2 is the insurance coefficient.
  For example, assume that the volume of a room is 700 m3. Before humidification is performed, the temperature is 25°C, and the relative humidity is 30% (the absolute humidity d2 is 5.983 g/kg as specified in the psychrometric chart). After humidification is performed, the temperature is 25°C, and the relative humidity is 50% (the absolute humidity d1 is 10.037 g/kg as specified in the psychrometric chart).
  Humidification capacity W = ρ x V x (d1 – d2) x 1.2 = 1.2 x 700 x (10.037 – 5.983) x 1.2 = 4.086 kg

## Slide 17: Task 3: Reference Layout
Solution layout (Illustration)
  Layout 1
  Layout 2
  Layout 3
Maximum number of cabinets
Best airflow organization
Average

## Slide 18: Task 3: Reference Layout
  Symmetric layout
  Unsymmetric layout

## Slide 19: Task 4: Discussing and Determining a Chilled Water System
Task description
  Discuss in groups about the following questions: According to the five classification methods of chilled water system of air conditioners in intensive lectures, what factors need and need not to be considered in the feasibility study phase when a chilled water system is selected in this project? If the chilled water system shown in the figure on the right is configured, can the system meet the fault tolerance requirement and why?
Task rules
  Each group discusses the two questions for 15 minutes and writes the discussion results on the electronic whiteboard.
  Each group presents its answers and reasons. Give 1 point for each correct factor.
Chilled water return
Chilled water
return
Chilled water supply
Chilled water supply
A/C: N+1
Chiller
Chiller
Chiller
Chiller
Secondary pump: N+1, N=3
Chiller: N+1, N=3
Primary pump: N+1, N=3
A/C
A/C
A/C
A/C
A/C

## Slide 20: Reference Answers to Task 4
Reference answer to question 1
  Closed or open chilled water system: The open chilled water system has a high lift and consumes a large amount of energy. Water in the cooling system is in direct contact with the air, which easily causes pipe corrosion.
  Supply or return water mode: Only cooling is considered for air conditioners in data centers. Therefore, two pipe systems are used.
  Direct return system or reverse return system: This item needs to be considered in the drawing design phase and is not considered in the feasibility study phase.
  Constant flow system or variable flow system: The water flow is determined according to the maximum load. The water supply volume of air conditioners is greater than that the water volume required by the actual load in most of the time. The energy consumption of the water pump is always in designed maximum value, which does not meet the energy saving requirements of the data center and needs to be considered.
  Primary pump system or secondary pump system: The secondary pump system can adapt to the situation with high differences in the lift capacity and water supply radius of each area. It can save the transmission energy, but the initial investment is large. The primary pump system is simple, but it cannot adapt to the situation with high differences in the lift capacity and water supply radius. It is applicable to small- and medium-sized cooling systems.

## Slide 21: Task 5: Selecting Devices and Optimizing the Chilled Water System
Task description
  Subtask 1: Assume that the chilled water in-row solution is selected and two chillers listed in the table are selected. Discuss in groups whether the chillers can meet the requirements.
  Subtask 2: If the data center is built in a subfrigid zone and the time when the temperature is lower than 20°C accounts for more than half of a year, what methods can be used to save energy and reduce the PUE?
  Subtask 3: If the customer uses the direct ventilation solution, calculate the required cooling capacity.
Task rules
  Group members discuss whether the chillers can meet the cooling requirements in the high-, medium-, and low-density areas, and whether the redundancy and device selection are reasonable. What are the supply and return water temperatures?
  Each group discusses and proposes some feasible energy-saving solutions from the perspective of the system.
  Discussion time: 20 minutes

## Slide 22: Reference Answers to Task 5
In winter, the outdoor low-temperature air can be used for cooling (known as free cooling technology).
  Add an energy-saving heat exchanger to the system. The heat exchanger is not used in summer. When the outdoor temperature is 2°C lower than the outlet temperature of the chillers, the central cooling system dissipates heat in the equipment room through the chilled water pipes, energy-saving coil pipes, and cooling tower to outdoors and reduces the equipment room temperature. In this way, the runtime of chillers can be reduced and the operating costs of the cooling system can be saved.
Variable-frequency water pump technology
  Variable-frequency pumps are commonly used in China. Compared with constant-frequency pumps, variable-frequency pumps feature less power consumption, regulated pressure function, less impact on the power system, less noise, and low temperature rise of pump motors. However, its investment is twice that of common constant-frequency pumps.
Optimized airflow organization in the equipment room
  Based on the rack layout and heat dissipation requirements, the low-density downflow air supply and upflow air return is used. In the high-density area, the cold aisle containment and in-row solution are adopted, and isolated aisles are configured. In the medium-density area, a proper airflow organization mode is used according to the heat dissipation capacity.
Optimized control policy: Improve the efficiency of the chillers and reduce the energy consumption of the water pump. Set the supply and return water temperatures to 10°C/16°C.
Notes: Pay attention to the use of the indirect evaporation technology and direct ventilation free cooling technology.

## Slide 23: Task 6: Providing Cooling System Configuration Suggestions
Task description
  According to the answers of tasks 1 to 5, determine the configuration of the cooling system and provide suggestions about the following aspects.
    Cooling source type: water-cooled cooling system or air-cooled DX system
    Energy-saving technical specifications: indirect free cooling technology or variable-frequency water pump technology
    Power density planning for a single cabinet
    Technology adopted to improve the utilization of cold air: Cabinets are deployed in face-to-face and back-to-back mode. In addition, the cold or hot aisle containment technology is used.
    The indoor units are configured in N+X mode by room or module.
    The pipes of the cooling system are deployed in redundant (or backup) mode.
    The cooling sources are also configured in N+X mode.
    Comprehensively consider system reliability and other requirements.
  Group members discuss and complete the table from the perspective of the system. Give 2 points to the group that completes the table.

## Slide 24: Task 6: Reference Table
Item | Description | Others
Configuration description |  | 
Power density planning for a single cabinet |  | 
Cooling source type |  | 
Cooling source of the air conditioner: configured in N+1 mode |  | 
Energy-saving technology |  | 
Airflow organization mode |  | 
The indoor units are configured by room or module. |  | 
Pipe deployment for the cooling system |  | 
Continuous cooling requirement |  | 
Restrictions on the onsite environment |  | 
Fresh air system |  | 
Exhaust system |  | 

## Slide 25
Answer the following questions:
If UPSs are deployed in the data center in this project, how to configure the air conditioners?
What are the causes for the difference between the load calculated in task 1 and the final load?
Notes: 1. UPS heat dissipation needs to be considered and calculated.
2.Different calculation coefficients and calculation methods are used. The supported power density is different.

## Slide 26
Calculate data center cooling system loads.
Select data center air conditioner configurations and optimize the configuration solution.
Understand the configuration and selection principles of a chilled water system and chillers.
Optimize a cooling system and understand its simple configurations.

## Slide 28
HCIE-DCF-Design
V1.0
Yuewenjun/wx507858
2020/10/7
Lishaofeng/00486775
2020/12/7