The project plane information is as follows:

The area is 7.9 m x 19.6 m. The area of high, medium, and low areas is basically the same. The low-density area has an open side. Due to the reconstruction layout solution, calculate the maximum number of IT cabinets supported by the area and obtain the specific load range. The vertical height of the equipment room is 4.5 m. Raised floors can be deployed.

The requirements for installing and deploying modules are as follows:

Single-row scenario

Single-row scenario

Dual-row scenario

Dual-row scenario

In single-row and dual-row scenarios, 2400 mm is reserved at the entrance, 1200 mm away from the wall, and the distance between modules is 1200 mm.

| Room Name | Number of cabinets | Power density of a single cabinet | UPS power | Simultaneous coefficient | comprehensive coefficient | Total cooling capacity |
| --- | --- | --- | --- | --- | --- | --- |
| High-density equipment room (R1) |  |  |  |  |  |  |
| Medium-density equipment room (R2) |  |  |  |  |  |  |
| Low-density equipment room (R3) |  |  |  |  |  |  |
| Total cooling load (kW) |  |  |  |  |  |  |

Modular load statistics table:

Note: The number of cabinets depends on the cabinet size, layout, and area of the cabinet. The power of a single cabinet depends on the services carried by the cabinet. For example, if the peak power of a blade server is greater than 10 kW, you can estimate and select the power based on the areas where the server is located, medium, and low. The typical power of storage devices is 7 kW, and the typical power of transmission devices is 5 kW.

| Item | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3kW |  |  |  |  |  |  |  |  |
| 4 kW |  |  |  |  |  |  |  |  |
| 5 kW |  |  |  |  |  |  |  |  |
| 6 kW |  |  |  |  |  |  |  |  |
| 7 kW |  |  |  |  |  |  |  |  |
| 8 kW |  |  |  |  |  |  |  |  |
| 10 kW |  |  |  |  |  |  |  |  |
| 12 kW |  |  |  |  |  |  |  |  |
| 14 kW |  |  |  |  |  |  |  |  |

Task 2: End Configuration Reference Table

Task 6: Configuration Suggestions

| Item | Description | Others |
| --- | --- | --- |

| No. | Item | Air conditioner load |
| --- | --- | --- |
| 1 | Air conditioner load in high-density areas |  |
| 2 | End configuration in high-density areas |  |
| 3 | (Optional) Chiller Configuration in High-Density Areas |  |
| Others |  |  |

The following uses a high-density area as an example. The cooling load and cooling source configurations are as follows: