## Slide 1: DC Facility Consultation and Planning Guide

## Slide 2
A data center (DC) is large in scale and complex in system structure. Based on service and management requirements, each related department will raise requirements on how to build a DC, where to build the DC, how much to invest, and how much to gain from the DC. Therefore, it becomes a very important issue for DC users to figure out how to sort out these different requirements scientifically, ensure the economical efficiency and reliability of the subsequent operation, and finally obtain the most appropriate overall solution.

## Slide 3
On completion of this course, you will be able to:
  Understand the overall DC planning and consultation service process.
  Know how to use the three DC assessment models.
  Be familiar with the approach for producing the DC site selection report and feasibility research report.

## Slide 4
DC Planning Process
DC Assessment Models
Site Selection Report
Feasibility Research

## Slide 5: Factors to Be Considered in DC Construction
Google DC in Finland
Facebook DC in Oregon
Alibaba Cloud DC beside Qiandao Lake
Tencent Guizhou Qixing DC
Apple Maiden DC
Notes: Google DC at Hamina port, Finland.The low-temperature seawater is transported from the Gulf of Finland to the cooling station of the DC through the circulating pump. The heat exchanger exchanges heat between the seawater and the chilled water in the DC. The temperature of the seawater increases after the seawater absorbs heat
Facebook DC in Oregon: It is located in the desert of Oregon in the US.The DC adopts various energy saving technologies, such as direct ventilation for free cooling, equipment room temperature improvement, double-layer ventilation structure, customized power modules unique battery rack and equipment rack design, power supply voltage improvement, and server virtualization technologies, to achieve a PUE of 1.07.
The Apple Maiden DC is located in North Carolina, where a long sunshine duration, a preferential policy for environmental protection, and cheap land are available. The DC uses PV power generation as the main energy source, to achieve zero emission and earn LEED Platinum.
Alibaba Cloud DC beside Qiandao Lake: The annual average temperature of the Qiandao Lake area is 17°C. The temperature of the deep water lake is constant all year round. The DC uses lake water cooling instead of air conditioner cooling for 90% of the year. The estimated annual average PUE of the DC is 1.3.
Tencent Guizhou Qixing DC: The DC will be used to store Tencent's core big data in the future. The DC features high concealment, high protection, and high security. Five caves were cut in a hillside about hundreds meter long, with two square shafts at the top of each cave.

## Slide 6: Factors to Be Considered in Requirement Analysis
External conditions
Area, floor, and bearing capacity of each functional area in the equipment room
Power supply and water supply environment
Weather, transportation, geology...
Service requirements
Power density (equipment information)
Business growth rate...
Customer expectations
Energy saving objective (PUE)
Construction level (Tier I–Tier IV, Class A/B/C)
Initial scale, reservation for capacity expansion
Resource usage (surface usage and cabinet space usage)
Management requirements (management objects, linkage requirements, and proactive management)
Display function (visualized O&M)...
Compliance
Availability
Functionality
Serviceability
Cost-effectiveness
Scalability
Energy saving
Security

## Slide 7: DC Requirement Analysis Methodology
How to optimize
Where to construct
Construction size
Why to construct
How to monitor
How to migrate services to the cloud
Business requirements
IT infrastructure requirements
Facility requirements
Planning model assessment
Design input
Hardware environment
Middleware
Cloud platform
Partners
Application services
Total cooling capacity
Spatial layout
Capacity expansion plan
Power density
Energy efficiency model
Economic model
Reliability model

## Slide 8: DC Consultation and Planning Process
The process from launch to project initiation for a DC involves a series of analysis and research, which is called the consultation phase. The feasibility research of the DC is also a task to be completed in this phase. Feasibility research is usually conducted after business consultation. The site selection and feasibility research are usually conducted in parallel and staggered. On one hand, the site selection result directly affects the technical solution of the DC. On the other hand, the requirements of the technical solution also affect the site selection.
Strategic
development plan
Business model
Service
development plan
Feasibility research
Site selection
Implementation plan
Service and operation assessment
Operation
environment analysis
Carrier analysis
+
Surrounding understand
and
inner assessment
Business plan
and
feasibility analysis
Implement plan
and
operating assessment

## Slide 9: Objectives of Site Selection
Site selection is a key decision in the DC planning phase. The result directly affects the service success of a DC.
Site selection is to select the best candidate site based on an experienced site selection team, scientific site selection methods, and professional site selection tools.
Key factors for site selection
Analysis and conclusion
Candidate solutions
Suggestions on site selection based on comprehensive analysis and considerations
Transportation
Environment
Considerations
Grid
Communications
Geology
Others
HVAC
Power
Risk
TCO analysis
PUE Analysis
Notes: Method
  Process and methods for site selection consultation
  Assessment standards for site selection consultation
  Assessment system for site selection consultation
Professional
  Experienced site selection consultation team
  Heating, ventilation and air conditioning (HVAC), heavy current, and weak current research team
Tool
  Global climate database
  Other databases
  Site selection consultation checklist

## Slide 10: Objectives of Feasibility Research
Feasibility research is the source of DC planning, design, and integration implementation. It analyzes factors that affect the project, such as technologies, laws, and regulations, determines whether the project is necessary and feasible, determines the technical solution to be used, and evaluates the economic and social benefits of the project, providing decision-making suggestions for project investors.
Requirement
analysis
Construction
plan
Investment decision making
Business/IT requirements
Equipment room level
Capacity
Capacity expansion plan
Power density
Energy efficiency level
Budget and economic analysis

## Slide 11
DC Planning Process
DC Assessment Models
  Reliability Model
  Energy Efficiency Model
  Economic Model
Site Selection Report
Feasibility Research

## Slide 12: Reliability and Availability
Failure rate: indicates the conditional probability that a component works normally before time t and becomes faulty after time t.
  λ = 1/MTBF
Reliability: indicates the probability that specified functions can
be performed under specified conditions.
  R = e–
  Serial system: R(t) = R(1) x R(2) = e–(1 + 2)t
  Parallel system: R(t) = R(1) + R(2) – [R(1) x R(2)],
  R(t) = e–1t + e–2t – [e–(1 + 2)t]
Availability: indicates the capability of performing specified functions under specified conditions at specified time or in a specified time range. It reflects the system reliability, repairability, and maintainability. Availability is usually represented by letter A.
MTBF: Mean Time Between Failures
MTTR: Mean Time To Repair
RLT: Repair Logistics Time
Availability =
MTBF
MTBF + RLT + MTTR
x 100%

## Slide 13: Availability and Reliability of DCs
The engineering construction standards related to DCs are the requirements and embodiment of the functions, design and deployment, construction techniques, and acceptance standards of DCs, and have specific requirements on the availability and reliability of DCs.
  GB 50174-2017
    The facilities of a Class A DC should be configured based on the fault tolerance system.
    The facilities of a Class B DC should be
    configured based on the redundancy requirements.
    The facilities of a Class C DC should be
    configured based on the basic requirements.
  TIA-942-2017
    Tier I – Basic site facilities
    Tier II – Site facilities for redundant capacity
    components
    Tier III – Concurrently maintainable site facilities
    Tier IV – Fault-tolerant site facilities
Reliability of data
center facilities
Equipment room location
Building structure
Power supply and distribution system
Cooling
system
Equipment room network
Integrated
cabling
...
Notes: In this course, only the reliability models of the power supply and distribution system and cooling system are discussed.

## Slide 14: Reliability Model of the Power Supply and Distribution System (1)
The following uses the typical architecture of the power supply and distribution system in a Tier IV disaster recovery (DR) DC as an example.
Availability of the uninterruptible power supply (UPS) AC input
  A1,1 = [1 – (1 – A1) x (1 – A2)] x A3 x A4
Availability of the UPS input power
  A1,2 = [1 – (1 – A1,1) x (1 – A5)2]
A1,2
A1,1
ATS
(A3)
LV
system
(A4)
UPS
battery
(A5)
UPS battery (A5)
UPS
battery
(A5)
UPS battery (A5)
UPS
(A6)
UPS
(A6)
UPS
(A6)
UPS
(A6)
PDU
(A7)
PDU
(A7)
STS
(A8)
Load A (dual power supplies)
Load A (dual power supplies)
Load A' (single power supply)
Mains
(A1)
D.G
(A2)
ATS
(A3)
LV
system (A4)
Main
(A1)
DG
(A2)
Notes: The Uptime class A DC power supply system consists of two mains power supplies, two backup power supplies, two LV power distribution systems, a UPS 2N system, and two PDU power distribution systems.

## Slide 15: Reliability Model of the Power Supply and Distribution System (2)
ATS
(A3)
LV
system
(A4)
UPS
battery
(A5)
UPS battery (A5)
UPS
battery
(A5)
UPS battery (A5)
UPS
(A6)
UPS
(A6)
UPS
(A6)
UPS
(A6)
PDU
(A7)
PDU
(A7)
STS
(A8)
Load A (dual power supplies)
Load A (dual power supplies)
Load A' (single power supply)
Mains
(A1)
D.G
(A2)
ATS
(A3)
LV
system (A4)
Main
(A1)
DG
(A2)
The following uses the typical architecture of the power supply and distribution system in a Tier IV DR DC as an example.
Availability of the UPS 2N system
  A6,1 = [1 – (1 – A6)2]
Availability of a bus power supply system
  A6,2 = A1,2 x A6,1 x A7
A1,2
A1,1
A6,1
A6,2
Notes: A bus power supply system consists of the UPS input power supply, UPS 2N system, and PDU power distribution system.

## Slide 16: Reliability Model of the Power Supply and Distribution System (3)
The following uses the typical architecture of the power supply and distribution system in a Tier IV DR DC as an example.
Therefore, the availability of the power supply system for key loads is as follows:
  A = [1 – (1 – A6,2)2] (dual power supplies), A' = [1 – (1 – A6,2)2] x A8 (single power supply)
A6,2
ATS
(A3)
LV
system
(A4)
UPS
battery
(A5)
UPS battery (A5)
UPS
battery
(A5)
UPS battery (A5)
UPS
(A6)
UPS
(A6)
UPS
(A6)
UPS
(A6)
PDU
(A7)
PDU
(A7)
STS
(A8)
Load A (dual power supplies)
Load A (dual power supplies)
Load A' (single power supply)
Mains
(A1)
D.G
(A2)
ATS
(A3)
LV
system (A4)
Main
(A1)
DG
(A2)
Notes: The Uptime class A DC power supply system consists of two mains power supplies, two backup power supplies, two LV power distribution systems, a UPS 2N system, and two PDU power distribution systems.

## Slide 17: Reliability Model of the Power Supply and Distribution System (4)
Refer to the related data in the table. The following can be obtained through calculation:
  Availability of the AC input power A1,1 = 0.9999 4144 6225 299
  Availability of the UPS input power A1,2 = 0.9999 9999 9999 983
  Availability of the UPS 2N system A6,1 = 0.9999 9999 7382 582
  Availability of a bus power supply system A6,2 = 0.9999 9876 0808 568
  Availability of key loads A = 0.9999 9999 9998 464 (dual power supplies),
  A' = 0.9999 9360 5155 464 (single power supply)
Subsystem | Power grid (A1) | Generator (A2) | ATS (A3) | LV power distribution system (A4)
Availability | 0.9988 1458 3841 | 0.9999 3202 0398 | 0.9999 4378 0437 | 0.9999 9774 6241
Subsystem | UPS battery (A5) | Single UPS system (A6) | PDU power distribution system (A7) | STS (A8)
Availability | 0.9999 8303 0881 | 0.9999 4883 9291 | 0.9999 9876 3426 | 0.9999 9360 5157
Reference values for the availability of major power supply subsystems and components
Notes: The Uptime class A DC power supply system consists of two mains power supplies, two backup power supplies, two LV power distribution systems, a UPS 2N system, and two PDU power distribution systems.

## Slide 18: Reliability Model of the Cooling System
The following uses the typical architecture of the cooling system in a Tier IV DR DC as an example.
Availability of the AC input power for each air conditioning system in the equipment room
  A1,1 = [1 – (1 – A1) x (1 – A2)] x A3 x A4
Therefore, the availability of the cooling system for key loads is as follows:
  A = [1 – (1 – A1,1 x A5)2] x A6
Subsystem | Power grid | Generator | High-power ATS
Availability | 0.9988 1458 3841 | 0.9999 3202 0398 | 0.9999 4378 0437
Subsystem | Air conditioning system of computer room air conditioners | LV power distribution system | Cabinet system
Availability | 0.9999 7333 4044 | 0.9999 9912 1013 | 1
Reference values for the availability of major
cooling subsystems and components
Mains
(A1)
D.G
(A2)
ATS
(A3)
LV
system
(A4)
ATS (A3)
LV
System
(A4)
air
conditioners
(A5)
air
Conditioners
(A5)
Cabinet system
(A6)
Key load A
A1,1
Mains
(A1)
D.G
(A2)
Notes: The cooling system (N+N fault tolerance configuration) of a Uptime class A DC consists of two mains power supplies, two backup power supplies, two LV power distribution systems, and two redundant cooling systems consisting of the air conditioning system dedicated for N+N redundancy equipment rooms and cabinet system.

## Slide 19
DC Planning Process
DC Assessment Models
  Reliability Model
  Energy Efficiency Model
  Economic Model
Site Selection Report
Feasibility Research

## Slide 20: Quantitative Assessment Indicators for DC Energy Efficiency – PUE
In 2006, Christian Belady put forward the concept of DC power usage effectiveness (PUE). In 2007, The Green Grid (TGG) developed and improved the concept of PUE. In February, TGG proposed the following PUE definition in Green Grid Metrics:
On October 29, 2009, TGG released the PUE white paper 2.1, that is, PUE v2, which is
frequently referenced. PUE v2 provides a method to report more accurate PUE. PUE V2
defines different types of PUE measurement methods. TGG divides these methods into
three levels: basic, intermediate, and advanced.
In 2011, the DC Efficiency Task Force (DCETF) published a paper outlining the
recommended methods for measuring and reporting PUE. DCETF adds a 4th level that is
more basis. From PUE0 to PUE3, a higher level indicates stricter requirements. Next, I will focus on PUE0, PUE1, PUE2, and PUE3 defined by DCETF.
PUE =
Total facility energy
IT infrastructure energy

## Slide 21: Four Levels of PUE V2
The following table lists the PUE levels in the Recommendations for Measuring and Reporting Overall DCs Efficiency released by DCETF.
Except for PUE0, all measurement results must be converted into energy, which means that time components must be introduced. An example is as follows: if kilowatts per hour is used to replace kilowatts, all input energy must be included. For example, heat generated by gas combustion must be converted into kilowatts per hour.
In addition, all measurement results must be measured at the specified time point for at least one year.
 | PUE0 | PUE1 | PUE2 | PUE3
Energy Consumption Measurement Position of IT Infrastructures | UPS output power | UPS output energy | PDU output energy | Input energy of IT equipment
Definition of IT Infrastructure Energy Consumption | Peak power of IT equipment | Annual energy consumption of IT equipment | Annual energy consumption of IT equipment | Annual energy consumption of IT equipment
Definition of Total Facility Energy Consumption | Peak power of total facilities | Annual energy consumption of total facilities | Annual energy consumption of total facilities | Annual energy consumption of total facilities

## Slide 22: Measuring Positions of IT Equipment Energy Consumption for Different Levels of PUE V2
According to PUE V2, the energy consumed by offices and network operations centers (NOCs) must be included in the PUE calculation formula.
PUE V2 also clarifies that renewable energy, such as wind and solar energy, has no impact on the PUE, and that the PUE is irrelevant to the energy source and type.
The four levels of PUE V2 are designed for new or reconstructed DCs. All-round measurement should be included in the design so that the DCs can become facilities with high energy efficiency.
PUE0/PUE1
PUE2
PUE3
 | PUE0 | PUE1 | PUE2 | PUE3
Measuring Positions of IT Equipment Energy Consumption | UPS output power | UPS output energy | PDU output energy | Input energy of IT equipment
Definition of IT Equipment Energy Consumption | Peak power of IT equipment | Annual energy consumption of IT equipment | Annual energy consumption of IT equipment | Annual energy consumption of IT equipment
Definition of Total Facility Energy Consumption | Peak power of total facilities | Annual energy consumption of total facilities | Annual energy consumption of total facilities | Annual energy consumption of total facilities

## Slide 23: Energy Efficiency Model – DC Energy Consumption Structure
Precision air conditioner
IT device
Humidifier
Chiller
PDU
UPS
Lighting and other devices
Power input
Switch/DG
Heat dissipation
Cooling system
IT device
Others
Source: The Green Grid
DC energy consumption structure: includes IT equipment energy consumption, power supply and distribution energy consumption, and cooling energy consumption.
  Power load factor (PLF) = Energy consumption of the power supply and distribution system/Energy consumption of IT equipment
  Cooling load factor (CLF) = Energy consumption of the cooling system/Energy consumption of IT equipment
  IT/IT indicates the ratio of the energy consumption of IT equipment to its own, that is, the value of IT/IT is 1.
Mains
UPS
PDU
IT
Cooling
PLF
IT
CLF
Energy efficiency model
Notes: The PUE of some DCs is calculated as follows: PUE = PLF + CLF + ALF + 1. The auxiliary load factor (ALF) is the energy efficiency factor of auxiliary systems such as the lighting system and office system. This part is not discussed in this course.

## Slide 24: Energy Consumption of IT Equipment
IT equipment in a DC includes servers, storage equipment, and LAN switches. The number of servers is the largest, occupying the majority. The energy consumption features of IT equipment are similar. Therefore, servers are used as an example.
  Rack servers are still the mainstream. Some high-end DCs use large servers such as midrange servers and mainframes.
  Mainstream public clouds, such as HUAWEI CLOUD, Alibaba Cloud, Baidu Cloud, Tencent Cloud,
  AWS, Microsoft, and Google, have provided GPU-based computing services.
  Huawei GPU server is 4 U high. The power of a single server is 4.4 kW. A maximum of 10 servers can be installed in a rack. The rated power density of the rack is 44 kW, and the actual power is about 30 kW.
  The rated power of HPE, SuperMicro, and NVIDIA products ranges from 3.2 kW to 4 kW, and the rack power can be greater than 30 kW.
The Huawei RH1288 V server is a 1 U 2-socket rack server. Its maximum power consumption is about 500 W (with 8 drives, 2 CPUs, and high load). If 40 U cabinets are fully configured, the power density can reach 20 kW.
Huawei E9000 blade server is 12 U high. Three servers can be deployed in one single rack. The rated power of the rack is 27 kW to 45 kW, and the actual operating power is about 17 kW.
Notes: Huawei RH1288 V3 server (RH1288 V3 for short) is a general-purpose 1 U 2-socket rack server launched to meet customer requirements for the Internet, Internet DC (IDC), cloud computing, enterprise, and telecom service applications.

## Slide 25: IT Equipment Energy Consumption – Annual Energy Consumption
Single server: Assume that the maximum output power of a 2 U server is 500 W and the AC/DC conversion efficiency is 85% (average value). The maximum input power Pserver of the server is calculated as follows:
  Pserver = Pmax/0.85 = 500 W/0.85 = 588.23 W, which indicates the maximum power consumption of the server under full configuration and 100% load.
Overall servers: The actual operating energy consumption is not the same. Designing a medium-sized DC usually involves thousands of servers. Assume that a DC requires 2000 rack servers based on service requirements. The redundancy coefficient C is 0.8, and the utilization coefficient K is 0.8.
  Pactual = Pserver x C x K x 2000 = 588.23 W x 0.8 x 0.8 x 2000 = 752.93 kW, which indicates the actual total power of servers in a medium-sized DC. If high-density blade servers or integrated cabinet servers are used, the total power will be lower and the equipment power density will be higher. However, the actual total power must be considered based on actual service conditions.
Annual energy consumption (based on PUE3): Based on the industry attributes of DC services (such as finance, ISP, and government), assume that the actual annual usage efficiency is 0.7 and the efficiency of the UPS and whole set of power distribution equipment is 0.9. The annual energy consumption is calculated as follows:
  E = (752.93 kW x 365 x 24 x 0.7)/0.9 = 5,129,963.06 kWh, which is the denominator in the PUE calculation of the energy efficiency model.
Notes: Annual electricity price: The annual electricity price varies according to the electricity price and policy environment in different regions, which is also an important factor in the energy efficiency model. Assume that the annual average electricity price of area 1 is CNY0.5 per kWh and that of area 2 is CNY0.6 per kWh. The annual electricity price difference between the two areas can reach CNY51.3 million.

## Slide 26: Energy Consumption of the Power Supply and Distribution System
PLF = ATS switching loss rate + LV power distribution system loss rate + UPS system loss rate + Power cable loss rate
  The ATS switching loss, LV power distribution system loss, and power cable loss are small, which are basically the cable metal voltage drop, cable contact point loss, and heat loss. The statistical data shows that the value ranges from 1% to 3%. The median value is 2%, that is, 0.02.
  PLF = UPS system loss rate + 0.02
  In the DC design, the UPS system loss varies according to the UPS power supply solution.
LV system
Mains
D.G
UPS
PDU
Server
ATS
ATS loss
LV system loss
UPS loss
Power cable loss

## Slide 27: Power Supply and Distribution Energy Consumption – UPS System Loss (1)
For details, see the (1+1) solutions of DC UPS actual power supply in ANSI/TIA-942–2017. The UPS efficiency varies depending on the load rate in different configuration modes. The following uses the (1+1) parallel system power supply solution as an example to discuss the loss rate of the UPS system in a DC.
  PLF = UPS system loss rate + 0.02

## Slide 28: Power Supply and Distribution Energy Consumption – UPS System Loss (2)
Assume that the actual total power of IT loads such as servers in a DC is 1000 kW and there are 10 smart modules of 100 kW. Each smart module is configured with two UPSs to form a （1+1） parallel system, and each UPS bears 50 kW load. The power supply time is set to 15 minutes based on the standard power supply time of the DC.
  In solution A, two 160 kVA UPSs of a certain model are used, and the output power factor is 0.9. The load rate is 34%, which is in the range of 25%–50%. Use the digital interpolation method to calculate the UPS loss rate. The calculated result is H = 0.0877.
  In solution B, two 200 kVA UPSs of a certain model are used, and the output power factor is 0.9. The load rate is 27%, which is in the range of 25%–50%. Use the digital interpolation method to calculate the UPS loss rate. The calculated result is H = 0.0937.
Load Rate | 0 | 25% | 50% | 75% | 100%
Loss Rate-H | - | 9.50% | 7.48% | 5.93% | 7.63%
Load Rate | 0 | 25% | 50% | 75% | 100%
Loss Rate-H | - | 9.63% | 6.37% | 5.88% | 7.17%
Solution A UPS efficiency table
Solution B UPS efficiency table
Notes: The UPS efficiency tables of solution A and solution B are actually measured by UPS manufacturer.
Interpolation calculation:
  A: When the load rate is 34%, the UPS loss rate is in the range of 25%-50%, H=(7.48%-9.50%)/(50%-25%)×(34%-25%)+9.50% =8.77%
  B: When the load rate is 27%, the UPS loss rate is in the range of 25%-50%, H=(6.37%-9.63%)/(50%-25%)×(27%-25%)+9.63% =9.37%

## Slide 29: Power Supply and Distribution Energy Consumption – UPS System Loss (3)
PLF = UPS system loss rate + 0.02
  Solution A (160 kVA, 1+1): PLF = （UPS system loss rate + 0.02）×2 = 0.216
  Solution B (200 kVA, 1+1): PLF = （UPS system loss rate + 0.02）×2 = 0.228
Therefore, in the 1+1 UPS power supply solution, the PLF change is only 0.006 due to the load rate of UPSs with different capacities, which has little impact on the PUE. In addition, the following information must be clarified:
  Compared with the configuration solution of two UPSs in this case, if one UPS is configured or the modular UPS solution is used to improve the UPS load rate, the UPS system loss will be smaller.
  If a large-capacity STS is installed on each UPS output bus, the PLF increases by 0.01–0.02.
  If a power distribution output cabinet with an output isolation transformer is configured, the PLF increases by 0.03–0.05 each time a transformer is added to the power supply loop.
  This calculation model does not include the conversion efficiency of mains input, that is, the conversion loss of 35 kV/0.4 kV or 10 kV/0.4 kV is not included.

## Slide 30: Energy Consumption of the Cooling System
The CLF focuses on the heat load in a DC. The main sources are shown in the figure on the right.
Equipment heat loads: Q1 = PIT x η1 x η2 (kW)
  η1 is the number of systems in use at the same time, and η2 is the comprehensive coefficient.
  Generally, the cooling capacity redundancy is considered. The value of η1 x η2 is 0.8.
Other heat loads: Q' = Σ (Q2–Q5) = Q1 x 15% = PIT x η1 x η2 x 15%
  The heat loads (Q2, Q3, Q4, and Q5) except Q1 account for a small proportion of the cooling energy
  consumption of the entire DC. The heat loads can be estimated based on 15% of the equipment heat loads.
The power of IT equipment in a DC is 1000 kW and remains unchanged annually. The direct expansion (DX) cooling solution and chilled water (CW) cooling solution are used for comparison. Assume that COP of the DX cooling solution is 3 and COP of the CW cooling solution is 5.8.
  DX cooling solution: CLP = PDX/PIT = (Q1 + Q2 + Q3 + Q4 + Q5)/COPDX/PIT = (η1 x η2 + η1 x η2 x 15%)/COPDX = 0.32
  CW cooling solution: CLP = PCW/PIT = (Q1 + Q2 + Q3 + Q4 + Q5)/COPCW/PIT = (η1 x η2 + η1 x η2 x 20%)/COPCW = 0.166
Therefore, in different cooling solutions with the same heat load, the CLF change in the PUE indicator is 0.154, which has a great impact on the PUE.
Equipment heat load Q1
Building structure heat load Q2
Lighting heat load Q3
Supplemented fresh air heat load Q4
Personnel heat dissipation load Q5
Notes: Q2 is 10% of the IT equipment load in the equipment room, and Q3 to Q5 is 5% of the IT equipment load. Therefore, the load coefficient of Q2 to Q5 is 15%.

## Slide 31: Quantitative Assessment Indicators of DC Energy Efficiency
Based on the preceding calculation results, the quantitative assessment indicators of DC energy efficiency can be obtained.
  Solution 1 [UPS (160 kVA) + DX cooling] PUEcase 1 = 0.216+0.320+1=1.536
  Solution 2 [UPS (160 kVA) + CW cooling] PUEcase 2 = 0.216+0.166+1=1.382
  Solution 3 [UPS (200 kVA) + DX cooling] PUEcase 3 = 0.228+0.320+1=1.548
  Solution 4 [UPS (200 kVA) + CW cooling] PUEcase 4 = 0.228+0.166+1=1.394
In this way, a DC with good design and operation can be obtained. When the cooling system is correctly configured, the power supply and distribution system is stable, and the impact of fresh air units and office energy consumption is not considered, the energy efficiency ratio should be less than 1.5. Based on the configuration combination of different solutions and the balance between DC services and other assessment models, an important basis is provided for subsequent DC design and implementation.

## Slide 32
DC Planning Process
DC Assessment Models
  Reliability Model
  Energy Efficiency Model
  Economic Model
Site Selection Report
Feasibility Research

## Slide 33: Economic Model of Data Center Facilitiy
The investment in Data Center Facilitiy is a considerable expenditure. The purpose of using the economic model is to minimize risks and improve economic benefits. The economic model here is not a macro-economic or micro-economic model, but a model for investment economic analysis and economic assessment in DC projects. Based on model analysis and assessment, an optimal solution is selected from multiple dimensions including comprehensive availability, energy efficiency, and other factors. It is an important basis for making decisions on the DC site selection report and feasibility research report.
The economic model tool is used to comprehensively analyze the cost and revenue of the DC.
Cost
Revenue

## Slide 34: Cost and Revenue (1)
In the economic model of a DC, the total cost of ownership (TCO) is classified into capital expenditure (CAPEX) and operating expense (OPEX).
TCO
CAPEX
Depreciation and amortization
Depreciation estimation
Amortization estimation
OPEX
Energy cost
Manpower cost
Training expenses
Equipment
maintenance
and update
cost
Finance expenses
Other expenses
Notes: Depreciation and amortization: Depreciation and amortization indicate that the assets among the years of the production and operation periods are allocated to account for the income tax payable and distributable revenues in the current year.
Depreciation estimation: Annual depreciation = (Original value of fixed assets – Estimated net residual value)/Depreciation period
Amortization estimation: Amortization refers to the allocation of one-time input expenses such as intangible assets and deferred assets. The nature of amortization is the same as that of depreciation of fixed assets. Annual amortization = Expenses to be amortized/Valid period of use
Energy cost: Servers, LAN switches, and computer room air conditioners are energy-consuming equipment. The energy load density of DCs is much higher than that of common office buildings and factories. Therefore, energy cost is a major part of the DC cost.
Manpower cost: DC personnel include information technology personnel and technical management personnel. The number of personnel depends on the scale of the project, the size of the information system, and the nature of the work. The cost includes salaries, bonuses, benefits, and various insurances.
Training fees: Training includes professional training for technical personnel and operation training for users, both of which require funds.
Equipment maintenance and update cost: The maintenance cost includes the cost of computer consumables, machine maintenance, accessory replacement, and purchase of small tools and software.

## Slide 35: Cost and Revenue (2)
Revenues in the economic model of a DC are relative to the operation mode of the DC. According to operation modes, DCs are classified into commercial DCs and self-used DCs.
Commercial DC – revenues
Cloud business
IT facility business
Self-used DC – revenues
Efficiency improvement
Management standardization
Non-economic indicator
Economic indicator

## Slide 36: Economic Assessment Methods for DCs (1)
Based on the characteristics and operation modes of DCs, there are two methods for economic analysis and assessment.
ROI for DCs
TCO for DCs

## Slide 37: Economic Assessment Methods for DCs (2)
TCO for DCs
  The TCO is proposed by Gartner Group in 1987 to analyze the direct and indirect costs of information technology or the entire lifecycle of a DC.
  A DC project is regarded as a service or product with a lifecycle. The cost (hardware, software, energy consumption, and O&M management) of the entire lifecycle can be calculated based on different planning solutions to obtain different TCO models. Then, a proper and minimum solution can be selected.
  The TCO is used to calculate the cost of a DC. The revenues of the DC
  and the impact of uncertainty in the future are not considered. Therefore,
  the TCO is not applicable to economic assessment of commercial DCs.
Planning
Design
Construction
Running
Assessment

## Slide 38: Economic Assessment Methods for DCs (3)
ROI for DCs
  Facing the huge market of commercial DCs, such as cloud service providers and hosting DCs, and the developed management, the accounting of the ROI is becoming more and more refined. The ROI qualitative analysis is to quantitatively analyze the profitability and development prospect of DCs. Based on the TCO, the ROI takes into account the analysis and assessment of economic revenues and non-economic revenues.
  In the actual application, the ROI can use the static assessment indicators and dynamic assessment indicators based on project characteristics.
  The static assessment indicator is a quick and common financial judgment method. The specific indicators include the payback period and ROI. This course will focus on this part.
  The dynamic assessment indicator takes into account the time value of the fund and all the economic data in the whole lifecycle of the project. The specific indicators include net present value, dynamic investment payback period, internal rate of return, net present value method, and internal rate of return method.
Summarizing and collating basic data
Preparing estimated financial and economic activity reports
Conducting financial analysis and assessment
Analyzing and evaluating non-economic benefits
Performing comprehensive analysis and assessment

## Slide 39: ROI for DCs (1)
The static assessment indicator is one of the simplest financial judgment methods, including the payback period and ROI.
The payback period is the time it takes for the cash flow of an investment project to be equal to the initial investment of the project. The unit of the payback period is usually year. The shorter the payback period, the higher the feasibility of the project, and this indicator is applicable to a short-term recovery investment plan.
  Payback period Pt: the period required for the net income of the project in each year to equal to the investments. C1: cash inflow
  C0: cash outflow
Notes: The ROI for DCs can be classified into static assessment indicators and dynamic assessment indicators.
  The static assessment indicator is one of the simplest financial judgment methods.
  The dynamic assessment indicator takes into account the time value of the fund and all the economic data in the whole lifecycle of the project. The direct indicator includes the net present value.

## Slide 40: ROI for DCs (2)
The payback period can be calculated in two ways:
  When the net revenue of each year is the same after the project is completed, the calculation formula is as follows:
  I:the total amount of funds invested in the project, A:the net cash flow of each year, and the investment recovery is completed in t year.
  When the net revenues of a project vary from year to year, the calculation formula is as follows:
The assessment standard is Pt ≤ Pc, indicating that the project is feasible. Otherwise, this project is infeasible. Pc is the expected payback period.
Absolute value of the accumulated net cash flow of the previous year
Net cash flow of the current year
  Pt = Year when the accumulated net cash flow starts to be positive – 1+
Pt =
I
A
Notes: Characteristics of the payback period: It features a clear and simple concept, and can reflect the risk of the project. However, the economic data after the payback period is not involved.

## Slide 41: ROI for DCs (3)
The ROI is an indicator of profitability. It is the ratio of the net income M of a project in the normal production year to the total investment K.
The assessment standard is E ≥ Ec, indicating that the project is feasible. Otherwise, this project is infeasible. Ec is the benchmark value of the ROI.
M
K
E = —— x 100%
Notes: Characteristics of the ROI: the economic data within the project cycle is not involved.

## Slide 42
DC Planning Process
DC Assessment Models
Site Selection Report
Feasibility Research

## Slide 43: Site Selection Contributing to Availability
Natural risk
Artificial risk
Earthquake
Flood
Hurricane
Air pollution
Artificial damages
Power supply interruption
The DC requires resources such as electricity and water mains as well as diesel fuel.
Artificial damages, such as violent attacks, terrorist threats, and thefts bring various DC losses.
Air pollution greatly shortens the lifecycle of IT equipment.
Although earthquakes are of low probability, they cause devastation to the DC.
Site selection without considering locally geographical conditions and drainage systems may cause water leakage or flood damages.
Hurricanes, typhoons, and tornadoes have the same impact on the DC as earthquakes.
DC services are affected by locally natural and facility conditions. Therefore, external risks must be prevented during site selection to minimize the probability of equipment failures.
The external risks that affect DC availability include earthquakes, floods, hurricanes, power supply interruption, artificial damages, and air pollution.
Why
What
How
DC site selection

## Slide 44: Site Selection Contributing to Lowering down the TCO
Construction cost
Equipment cost
CAPEX
OPEX
Installation cost
Electricity cost
Broadband cost
O&M personnel cost
Tax
TCO
DC site selection assessment factors
Land price
Commodity
price
level
Natural cooling
Electri.price
Bandwidth rental price
Manpower cost
Tax policy
DC site selection determines the construction and operating costs. An optimal DC site enables the customer to achieve obvious economic benefits.
In the site selection phase, investigate information about the tax and manpower, bandwidth, and electricity costs, and assess the TCO of each candidate site as the essential decision-making basis.
Why
What
How

## Slide 45: Importance of Site Selection Consultation
DC lifecycle
Operating
Planning and design
Site
selection
Integrated implementation
Site selection is the initial phase of the DC lifecycle. Therefore, incorrect site selection will cause increasing losses in the following phases of the lifecycle.
Why not increasing investment by 20% in the site selection phase to prevent 80% of losses?
DC site
Cost
Risk
Revenue
Continuity
DC site selection affects costs, profits, service continuity, and risks of a DC. To select a proper site, experienced site selection consultants must perform objective analysis using scientific consultation methods and professional site selection tools.
Why
What
How

## Slide 46: Three Elements of Site Selection Consultation
Green
Availability
Low
costs
Site selection team
Site selection tool
Site selection method
Site selection
requirements
Experienced consultation team
HVAC, electrical, and extra low-voltage (ELV) survey team
Site selection consultation process and methods
Assessment standards of site selection consultation
Assessment system of site selection consultation
Global climate database
Other databases
Site selection consultation checklist
The site selection team, site selection method, and site selection tool are the three key elements of the site selection consultation service.
Consultation services are not delivered based on standardized operations, but largely depend on consultants' personal capabilities.
Methods and tools are also important to make assessment results more scientific and objective.
Why
What
How

## Slide 47: International Standard – ANSI/TIA-942 (1)
The local utility company should be able to provide adequate power to supply all initial and future power requirements for the DC.
The site should not be located in a 100-year flood plain, near an earthquake fault, on a hill subject to slide risk, or downstream from a dam or water tower. Additionally there should be no nearby sites that could create falling debris during an earthquake.
The site should not be in the flight path of any nearby airports.
The site should be no closer than 0.8 km (1/2 mile) from a railroad or major interstate highway to minimize risk of chemical spills.
The site should not be within 0.4 km (1/4 mile) of an airport, research lab, chemical plant, landfill, river, coastline, or dam.
The site should not be within 0.8 km (1/2 mile) of a military base.
Source: ANSI/TIA-942-2017
Telecommunications Infrastructure Standard for DCs
Why
What
How

## Slide 48: International Standard – ANSI/TIA-942 (2)
The site should not be within 1.6 km (1 mile) of nuclear, munitions, or defense plants.
The site should not be located adjacent to a foreign embassy.
The site should not be located in high danger and pollution areas.
The DC should be located below 3050 m (10,000 ft.) elevation.
Consideration should be given to zoning ordinances and environmental laws governing land use, fuel storage, sound generation, and hydrocarbon emissions that may restrict fuel storage and generator operation.
Source: ANSI/TIA-942-2017
Telecommunications Infrastructure Standard for DCs
Why
What
How

## Slide 49: DC Site Selection Assessment System (1)
Why
What
How

## Slide 50: DC Site Selection Assessment System (2)
Earthquake...
Tornado/Typhoon/Hurricane...
Connecting to multiple substations
Road facilities...
Dust, oil fume, harmful gas...
Factory storing explosive objects
Flat structure...
Construction materials...
Land price...
Electricity price...
Hosting service...
Virtual resource rental service...
IT service provider...
Infrastructure service provider...
Crime rate...
Terrorist threat...
Skill level...
Availability...
Backbone node or not...
Multi-operator link...
DC Site Selection Assessment System
Natural and geographical conditions
Facility conditions
Surroundings
Building structure
Cost factors
Market conditions
Business environment
Public security
Social resources
Network connectivity
Why
What
How

## Slide 51: How to Set Weights of Assessment Factors
Weights of factors in the assessment system are set based on customer's requirements. Do not apply the same factor weight configuration to all projects.
For example, the customer focuses on the availability, cost, and energy conservation of the DC in a project. Therefore, the association between each factor in the assessment system and the three features must be analyzed. Higher score indicates closer association, and then the weight of each assessment factor is obtained based on the score.
 | Association with Availability | Association with Costs and Profits | Association with Energy Conservation | Total Score | Weight
Natural and geographical condition | High | Low | High | 4 | 13.3
Facility condition | High | Medium | High | 5 | 16.7
Surroundings | High | Medium | High | 5 | 16.7
(Optional) Building structure | Medium | Low | Medium | 2 | 6.7
Cost factor | Low | High | Low | 2 | 6.7
Market condition | Low | High | Low | 2 | 6.7
Business environment | Medium | High | Low | 3 | 9.9
Public security | High | Low | Low | 2 | 6.7
Social resource | Low | High | Low | 2 | 6.7
Network connectivity | High | Medium | Low | 3 | 9.9
Correlation: High, medium, and low
Score: High = 2, medium = 1, low = 0
Why
What
How

## Slide 52: Site Selection Factor – Natural and Geographical Conditions (1)
A DC must be located in areas with less natural disasters, such as earthquakes, typhoons, and floods, to avoid devastation to the DC.
A DC should be located in cold and dry areas to minimize energy consumption.
Flood
Hurricane
Earthquake
Mudflow
Why
What
How

## Slide 53: Site Selection Factor – Natural and Geographical Conditions (2)
Natural Condition Assessment Factors | Assessment Standard
Earthquake | The site should be far away from seismic belts. According to the global seismic hazard map, the site should be located in areas where the seismic hazard degree is less than 4.0. The site should be far away from volcanoes. The site should be far away from sites that could create falling debris during an earthquake
Flood and tsunami | The site should be far away from areas where floods or tsunamis ever occurred within last 100 years. According to the global flood hazard distribution, the site should be located in areas where the flood hazard frequency is below 1st to 4th deciles, that is, the site is located in the white areas.
Mudflow | The site should be far away from a hill subject to slide risk, or downstream from a dam or water tower.
Hurricane, typhoon, and tornado | The site should be located in areas where the Saffir-Simpson hurricane intensity scale (SSHS) level is lower than SS1.
Altitude | The site should be located below 3050 m (10,000 ft.) elevation.
Climate | The site should be located in areas where the annual average temperature is below 20°C to achieve energy conservation using natural cooling sources.
Why
What
How

## Slide 54: Reference Data of Other Natural Conditions
Besides earthquakes, other natural disasters, such as hurricanes, mudflows, and tsunamis, must be considered. A DC should be far away from areas where these natural disasters are frequent.
In addition, climate conditions must be prioritized during DC site selection.
Flood
Hurricane
Temperature
Humidity
Tsunami
Why
What
How

## Slide 55: Site Selection Factor – Facilities (1)
DC's requirements for local power supply capability depend on the DC service characteristics, quality, and capacity. The power supply must be stable and sufficient.
The power quality affects DC operating. Frequent power outage, harmonic interference, and voltage peak may cause DC equipment failures
The power cost accounts for over 50% of the total DC operating cost, and therefore the mains price is important for DC site selection.
To ensure reliable DC operating and reduce the OPEX, a DC should be located in areas with sufficient and stable power supply, as well as low power cost.
Why
What
How

## Slide 56: Site Selection Factor – Facilities (2)
Facility Assessment Factor | Assessment Standard
Mains introduction | The site should be located in areas where power is sufficient and can be obtained from two or more substations. The power supply is not rationed even in peak hours in summer.
Road facilities | There are more than two separate roads routed through the site.
Water supply assurance | Water supply is sufficient.
Diesel fuel supply | The site should be within 20 km of diesel stations
Drainage facilities | Water leakage should be prevented in rainy days.
Besides power supply facilities, infrastructure such as water, road, and drainage facilities must be included in the DC site selection plan. Lack of any preceding facilities may cause problems in the maintenance phase.
Renewable energy
Traffic road
Why
What
How

## Slide 57: Site Selection Factor – Surroundings (1)
Air pollution, electromagnetic interference (EMI), and flammable and explosive objects are key elements to be focused in the surroundings of a DC.
Air pollution
EMI
Flammable and explosive objects
Hazard materials such as particles and sulfur in the air corrode equipment in the DC, which result in equipment failures and shorten the equipment service life. Therefore, air quality is a key element for site selection.
Severe EMI affects internal communications of the DC. It is recommended that a DC be located in a MICE M1I1C1E1 environment (according to ANSI/TIA-568-C.0).
A DC should be far away from factories and plants manufacturing or storing flammable and explosive objects.
Why
What
How

## Slide 58: Site Selection Factor – Surroundings (2)
Ambient Environment Assessment Factor | Assessment Standard
Air pollution | The air corrosiveness of the DC surroundings should meet the G1-level requirements specified in ANSI/ISA-71.04. The air cleanliness of the DC surroundings should meet the level-8 requirements specified in ISO 14644-1. The site should be far away from a heavily polluted source, such as a chemical plant, power station, coal mine, or electroplate factory. The site should be no closer than 0.8 km (1/2 mile) from a railroad or major interstate highway to minimize risk of chemical spills.
Factory with explosive materials | The site should not be within 1.6 km (1 mile) of nuclear, munitions, or defense plants.
EMI | It is recommended that a DC be located in a MICE M1I1C1E1 environment (according to ANSI/TIA-568-C.0).
Other risky factors | The site should not be in the flight path of any nearby airports. The site should not be within 0.4 km (1/4 mile) of an airport, research lab, chemical plant, landfill, river, coastline, or dam. The site should not be within 0.8 km (1/2 mile) of a military base. The site should not be located adjacent to a foreign embassy.
Why
What
How

## Slide 59: Site Selection Factor – Surroundings (3)
Air particle
Why
What
How

## Slide 60: Site Selection Factor – Building Structure
Compared with commercial buildings, DC buildings have requirements on the story height, bearing capacity, span, and materials.
Large-span buildings are recommended to facilitate equipment arrangement.
The bearing capacity of the building should meet requirements of the TIA-942 standards.
If a DC is located on the top floor of a multi-tenant building, sufficient vertical shaft and pipeline space should be reserved for power cables, ground cables, and air conditioners.
The building should meet the bearing requirements of equipment.
Building materials should be incombustible. The external wall should be constructed using concrete or ashlar masonry to ensure safety.
Large-span steel buildings are more suitable for DC equipment rooms.
Why
What
How

## Slide 61: Site Selection Factor – Costs (1)
Site selection affects the DC operating costs. Therefore, during site selection, consider impact of the land price, electricity price, broadband cost, manpower cost, and tax on the TCO.
The electricity cost occupies a high proportion of the total cost. The mains prices outside China are provided in the following slide for reference. The land price and manpower cost must be surveyed locally.
ROI
TCO
CAPEX
OPEX
Revenue
Forecast
Design
L0: land and buildings
L1: racks, air conditioners, and power supply equipment
L2: servers, storage, security, networks, and software systems
L3: service systems
Others: integration and deployment cost, manpower cost, and transportation cost
Electricity price
Bandwidth rental cost
O&M management cost
Sales cost
Tax cost
Other costs
Cloud services: cloud host, hard disk, and storage revenues
Traditional services: equipment room and equipment rental, bandwidth, and IP revenues
Value-added services
Product leasing rate
Tax rate and discount rate
Sales strategy
Product pricing
Product pattern
Product tariff package
ROI = TCO + Revenue = CAPEX + OPEX + Revenue
Why
What
How

## Slide 62: Site Selection Factor – Costs (2)
Source:
Global electricity prices
Why
What
How

## Slide 63: Site Selection Factor – Market Conditions (1)
Besides cost factors, local market conditions affect DC profits.
A survey on the local market conditions of various DC services is required to predict the market growth rate.
  Market conditions of the hosting service
  Market conditions of the virtual resource rental service
  Market conditions of value-added cloud services
  Market conditions of other cloud services
ROI
TCO
CAPEX
OPEX
Revenue
Forecast
Design
ROI = TCO + Revenue = CAPEX + OPEX + Revenue
Why
What
How

## Slide 64: Site Selection Factor – Market Conditions (2)
Market requirement analysis
Enterprise status
DC status
Future requirements
Industry
Area
Enterprise scale (employee quantity)
Main service
Service scale (or data scale)
Infrastructure
  Area and equipment room idleness rate
  Equipment room level
  Total rated power
  Telecom operator connection status
DC application
  Purpose (for production or DR)
DC overview
  Construction time
  Construction mode (self-built or outsourcing)
  Investment scale
Investment estimation (time and expected scale)
Expected investment field (for production or DR)
Outsourcing probability
Reason for outsourcing or not
Factors for selecting an outsourcing supplier: hardware conditions, service level, quality certification, and brand awareness
+
+
Survey content
Requirement scale, time, and purpose analysis
Customer group analysis
Required product and price
Local geographical conditions and policy advantages
Survey conclusion
Why
What
How

## Slide 65: Site Selection Factor – Market Conditions (3)
The costs and market conditions are analyzed to estimate the ROI of the project. The following describes a typical ROI analysis model for reference.
Go-to-market product
  Sales strategy
  Product pattern
  Product tariff package
CAPEX
  Equipment investment
  System integration
Key financial indicators
NPV
Gross profit margin
IRR
OPEX
  Equipment energy consumption
  Air conditioner cooling
  Equipment room space rental
  Equipment room facility rental
  Bandwidth rental
  System maintenance
  After-sales service (maintenance warranty)
  Market promotion cost and sales commission
Revenue
  VM leasing
  Storage leasing
  Value-added service leasing
Network KPI
  Virtual machine (VM) specifications
  VM scale
  Storage scale
  Network bandwidth
  Market analysis
  Application scenarios
  Network development scale
  Product leasing rate
  Tax rate
  Discount rate
Why
What
How

## Slide 66: Site Selection Factor – Business Environment
DCs are not isolated, and must be located in areas with suitable business environments.
To select a site, investigate local IT service providers, infrastructure service providers, security services, property rental resources, living facilities, and transportation resources.
DC
IT service provider
Security service
Property rental
Infrastructure service provider
Living facility
Transportation
Why
What
How

## Slide 67: Site Selection Factor – Network Connectivity
Network connectivity determines the DC reliability. To ensure smooth DC data output, a DC should be located in areas with network coverage of multiple operators.
The network bandwidth affects the customer experience. The output bandwidth of existing IDCs is generally 100 Gbit/s or above, and the bandwidth requirements will be increased gradually.
Why
What
How

## Slide 68: Site Selection Consultation Service Process (1)
The service process of DC site selection consultation varies with projects. However, the service process mainly includes the following three phases based on summarized site selection consultation experience:
Preparation phase: Understand requirements and formulate plans.
Research phase: Perform survey and research and collect information.
Analysis phase: Analyze and output assessment results.
Why
What
How

## Slide 69: Site Selection Consultation Service Process (2)
High-level presentation
Overall
analysis
TCO analysis and comparison
PUE analysis and estimation
Risk recognizing and assessment
Surrounding survey
Site survey
Site selection plan formulation/
Site selection team establishment
Assessment system determination based on business requirements
Natural and geographical data collection
Municipal condition research
Service development research
Site selection checklist
Candidate site assessment table
Site selection assessment report
Preparation phase
Research phase
Analysis phase
Consultation process
Output
Candidate site
Service planning
Input
Requirement understanding and clarification
Why
What
How

## Slide 70: Service Contents in the Preparation Phase
Requirement understanding and clarification
Assessment system determination
Site selection plan formulation/Site selection team establishment
Fully understand service requirements, formulate site selection assessment systems and plans, and assign task owners.
Get familiar with customer's services and (IDC) development plans:
Project budget
Potential user groups and user requirements
Project business mode
PUE of the existing IDC
Operating difficulties of the existing IDC
...
Determine the site selection assessment system that meets customer's requirements:
Natural and geographical conditions
Facility conditions
Surroundings
Cost factors
Market conditions
...
Formulate the site selection consultation plan, prepare required resources, and assign responsible personnel:
Organization of the team for site selection consultation
Site selection implementation plan
Consultation tool preparations
Why
What
How

## Slide 71: Service Contents in the Research Phase
Site survey
Social research
Data collection
Investigate local conditions and surroundings of the candidate site:
Location and geography
Ground resistance, load-bearing capability, and water quality
Transportation, mains, drainage, and broadband
Air pollution, noise, and EMI
Natural cooling source
...
Get familiar with information about local policies, prices, and social resources:
Land price
Prices of the mains, water, fuel, and natural gas
Tax policy
IDC market conditions
Business environment
...
Collect climate data and historical data of natural disasters:
Detailed climate data
Sunshine data
Historical data of natural disasters, such as earthquakes, floods, and hurricanes
Crime rate
...
Perform survey and research on candidate sites against the checklist based on requirements of the project assessment system.
Why
What
How

## Slide 72: Service Contents in the Analysis Phase
Analyze the survey and research data, score candidate sites, and output the assessment report to support decision making on DC site selection.
PUE analysis and estimation
TCO analysis and comparison
Risk recognizing and assessment
Analyze factors impacting PUE and PUE comparison results of each candidate site, and select a candidate site with the optimal PUE status:
Climate comparison for candidate sites
Impact of local climate conditions on the PUE
PUE analysis and comparison
...
Analyze the CAPEX and OPEX of candidate sites and select a candidate site with the optimal TCO:
CAPEX comparison for candidate sites
OPEX comparison for candidate sites
Recognize potential risks of candidate sites and select a candidate site with minimal risks during the construction and operating phases:
Damage risks caused by natural disasters
Equipment failure risks caused by air pollution
Tier-level recommendations
...
Risks
Why
What
How

## Slide 73: Deliverable of the Site Selection Consultation Report
Site Selection Consultation Report Deliverable
XXX Data Center
Site Selection Consultation Report
Why
What
How

## Slide 74
DC Planning Process
DC Assessment Models
Site Selection Report
Feasibility Research

## Slide 75: Principles and Contents of Feasibility Research
Why
What
How
Customer requirements differ, but the principles for DC project planning are almost the same.
DC
Regulation
Scalability
Economy
Serviceability
Function
Availability
Resource capacity, redundancy, backup, multiple routes, 7 x 24 x 365...
Flexible expansion, horizontal and vertical capacity expansion based on service requirements...
Scalability
Space design, functional area setting, service process compliance, flexible combination...
Function
Energy conservation, environment friendliness, automatic running, centralized control...
Economy
Controllability, facility monitoring, IT monitoring, operation services...
Serviceability
Law, regulation, industry standard, and security requirement compliance
Regulation
Availability

## Slide 76: Feasibility Research Plan Formulation
Project Preparation
Project Delivery
Project plan
Research result
Research report
System long-term objectives confirmed by customers
Consultation report draft
Consultation report draft review (presentation to middle-layer leaders)
Final feasibility report (presentation to executives)
Project initiation
Survey and research
Requirement analysis
Solution verification
Feasibility research report
Preliminary solution conclusions, suggestions, and economic analysis
Customer communication and confirmation
Report drafting
Feasibility research report presentation to middle-layer leaders
Project resource preparation
Project team establishment
Project scope (details) definition determination
Communication and determination of the project scope
Requirement research plan customization
Definition of the feasibility research plan
Onsite survey
Customer interview
Information research and collection (IDC situation, customer type, sales type, and IDC O&M situation)
Key problem discussion and clarification
Customer expectation research
Requirement analysis
Long-term objective communication and confirmation
Gap analysis
Preliminary analysis results
Feasibility research report presentation to executives
Final report submitting
Customer resource preparation and confirmation
Project kick-off meeting
Research material preparation
Executive seminar
Project principle and direction confirmation
Assessment range and framework communication
Assessment schedule communication
Project direction determination by the management layer
Project kick-off meeting
Executive communication
Consultation preparation
Principle and direction
Key project activities
Key achievements
W1
W2
W3
W4
W5
W6
W7
W8
W9
W10
W11
W12
W-4
W-3
W-2
W-1
Feasibility research plan formulation: project progress and work breakdown of feasibility research consultation services
Why
What
How

## Slide 77: Requirement Research
Based on different interviewees, formulate appropriate questionnaires to quickly and effectively learn customer status and requirements.
The customer interview is a cyclic iteration process and the PDCA method is adopted.
Customer executives
Planning & Construction Dept
O&M Center
Marketing department
Group account department
Network Construction Room
Key staff A
Strategy and vision
Positioning and objective
Business planning, requirements, and situations
General manager
Head of the Division
Chamber manager
Key employees
Questionnaire
+
Presentation
Questionnaire
+
Group discussion
+
Interview
Why
What
How

## Slide 78: Customer Interview Methods
Preliminary design of interview questions and materials
Initial communication with customers
Effect analysis
Material problems
Communication problems
Deep communication with key customers
Customer problems and opinion summary
Project scope confirmation and requirement research report output
D
C
P
A
Optimization
N
Y
Why
What
How

## Slide 79: Feasibility Research Service Contents
Risk analysis: Market analysis, technical risks, and project construction risks
Countermeasures
Environment and building structure planning
Construction standard planning
Electrical system planning
HVAC system planning
CAPEX estimation
OPEX estimation
TCO estimation
Construction scheme
Investment estimation
Milestones
Risk analysis
Three phases: preparation phase, research phase, and analysis and validation phase
Financial assessment
Social benefit assessment
Application scenarios
Building DC
Warehouse DC
Container DC
Prefabricated DC
Why
What
How
Economic assessment

## Slide 80: Feasibility Research Construction Scheme – Construction Standard Determination (1)
Reference design standards
Product documentation
Uptime Institute
ASHRAE TC 9.9
EIA/TIA-942
GB 50174
Industry guidance
International standards
ISO/IEC IS 11801
International standards
CENELEC EN 50173
North American standards
EIA/TIA-568A/B/C
Why
What
How

## Slide 81: Feasibility Research Construction Scheme – Construction Standard Determination (2)
Power Supply System | Construction Standards
External mains supply | Two independent power supplies
Transformer | 1+1
HV power distribution system | 1+1
LV power distribution system | 1+1
HV generator set | N+X
UPS system | 2N dual-bus system
Battery backup time | Backup duration of each UPS ≥ 30 min
Why
What
How

## Slide 82: Feasibility Research Construction Scheme – Construction Standard Determination (3)
Refrigeration System | Construction Standards
Natural cooling source | Adopted
Continuous cooling | Based on IT equipment requirements, consider whether to use continuous cooling for all IT equipment or some IT equipment.
Cooling equipment configuration | N+X redundancy (X = 1 to N)
Cooling pipes | Consider system reliability and redundancy.
Cabinet layout | Layout of cold and hot aisles
Air conditioner in the equipment room | N+X redundancy (X = 1 to N). X air conditioners work in redundancy mode in each air conditioning area in the computer room.
Water storage | Water assurance based on independent dual-municipal water or stored water
Why
What
How

## Slide 83: Feasibility Research Construction Scheme – HVAC System Architecture Determination
Precise upflow
Precise downflow
Cold aisle containment
Hot aisle containment
Air intake cooling
Cabinet-level liquid cooling
Equipment room-level liquid cooling
Partial liquid cooling of a cabinet (gas and liquid combination)
Direct ventilation
Rotary-wheel air conditioner
Chilled water + plate heat exchanger
Airflow distribution and management
Proper use of natural cooling sources
Multi-level liquid cooling
Why
What
How

## Slide 84: Feasibility Research Construction Scheme – CFD Simulation for Solution Selection
Method 1:
Without aisle containment
Method 2:
With aisle containment
Without aisle containment: The temperature at certain areas is close to 40°C, causing a high temperature only in some areas and unbalanced temperature fields in areas outside the positions for installing cabinets in an equipment room.
Aisle containment: The temperature in the entire equipment room is not higher than 26.6°C. The temperature field is relatively balanced for areas outside the positions for installing cabinets in the equipment room.
Why
What
How

## Slide 85: Feasibility Research Construction Scheme – Energy Saving Scheme
Power conversion, transmission, and distribution
IT equipment load
Cooling equipment load
Energy saving measures
Precise equipment load management chip design
IT equipment innovation (server, storage and network security)
Airflow organization optimization
Efficient air conditioner
Fresh air energy-saving technology
Liquid-cooling heat-dissipation solution
High-density cooling solution
Ice storage solution
Efficient and modular UPS system
HVDC
HV diesel generator (DG) power supply system
Renewable energy utilization
Intelligent lighting system
Waste heat recovery
Modular solution
Container solution
Green energy
Unified intelligent monitoring and management
E2E energy-saving design for DCs:
  IT system energy saving: Energy is saved from the beginning, involving use of low-power consumption chips, virtualization/distributed technology, and load balancing management
  Power distribution system energy saving: With reliability ensured, improve the power distribution efficiency to reduce the power consumption
  Refrigerating system energy saving: Involve airflow distribution design and use of the efficient refrigerating system and free cooling.
  Cabinet system energy saving: Ensure reasonable distribution of high- and low-density cabinets, cold/hot-aisle containment system, and precise air supply.
Why
What
How

## Slide 86: Feasibility Research Consultation Service – Delivery Process
  Information collection
  Requirements survey
Workshop
  Feasibility research report presentation to middle-layer leaders (1)
Workshop
  Feasibility research solution presentation to middle-layer leaders (2)
Workshop
  Feasibility research report presentation to executives
Workshop
  Feasibility research report
Result approval
Theme technologies and solutions are discussed by a hierarchical organization from the lower level to the top level on a workshop. In addition, an agreement is reached, indicating that deliverable delivery is complete.
Why
What
How
Conclusion and
suggestion
Construction scheme
Onsite survey
Feasibility plan formulation
Feasibility Report
Consultation process
Deliverable
Business planning
Business plan
Economic analysis
Investment estimation
Risk analysis
Requirement analysis
Project planning
Task understanding and clarification
Input
Municipal condition research

## Slide 87: Feasibility Research Construction Scheme – Electrical System Planning
No. | Equipment | Rated Load (kW) | Demand Coefficient | PF | Load Requirement |  | 
 |  |  |  |  | P | Q | S
 |  |  |  |  | (kW) | (kVar) | (kVA)
1 | IT load | 4800 | 1.00 | 0.95 | 4800.0 | 1577.7 | 5052.6
2 | Chiller | 1965 | 0.67 | 0.80 | 1316.6 | 987.4 | 1645.7
3 | Water pump and cooling tower | 930 | 0.67 | 0.95 | 623.1 | 204.8 | 655.9
4 | Air conditioner in the electricity room | 40 | 0.70 | 0.95 | 28.0 | 9.2 | 29.5
5 | Battery charging | 533.2 | 0.90 | 0.95 | 479.9 | 157.7 | 505.1
6 | UPS loss | 418.4 | 0.90 | 0.95 | 376.6 | 123.8 | 396.4
Electrical load calculation
Key technology analysis and system selection
Based on business requirements and IT planning, determine the power load of each system:
Calculate the IT equipment loads.
Calculate engine equipment loads, such as loads and loss of the air conditioner and electrical equipment.
Determine the capacity of the mains supply.
Based on service requirements, determine the power supply system architecture and key equipment models:
Architecture of the power distribution system – Tier III/Tier IV system architecture design
Model selection and analysis on advantages and disadvantages of technical solutions for the key equipment, such as the DG, transformer, UPS, and power distribution cabinet
Why
What
How

## Slide 88: Feasibility Research Construction Scheme – HVAC System Planning
Based on business requirements and IT planning, determine the power load of each system:
  Calculate the IT equipment loads.
  Calculate the loads of electrical equipment, such as the UPS.
  Calculate the water amount.
Light-colored areas refer to areas with rich natural cooling sources.
Heavy-colored areas refer to areas where mechanical cooling sources are used with restrictions.
Based on service requirements, determine the air conditioning system architecture and key equipment models:
  Architecture of the air conditioning system – Tier III/Tier IV system architecture design/cooling source selection analysis
  Model selection and analysis on advantages and disadvantages of the technical solutions for key equipment, such as the chiller, air conditioner, and water pump.
Why
What
How
Calculation of air conditioner loads
Key technology analysis and system selection

## Slide 89: Feasibility Research – Risk Analysis
Occurrence probability: high
Risk loss: small
Loss
Occurrence probability: high
Risk loss: large
Occurrence probability: low
Risk loss: small
Occurrence probability: low
Risk loss: large
Risk occurrence probability
Large
Small
Small
Large
Quadrant II
Quadrant I
Quadrant III
Quadrant IV
Market risk analysis
Technical risk analysis
Project construction risk analysis
The risk identify and quantum (RIQ) model helps identify potential market risks, technical risks, and project construction risks to minimize the impact of the negative factors.
The RIQ, a risk identification and quantification model, is used to identify project risks and calculate project loss caused by risks.
Quadrant | Importance | Measure
I | High | Disassemble high risks by key step.
II | Relatively low | Develop measures for reducing the risk occurrence probability.
III | Low | Extract the risk contingency.
IV | Relatively high | Develop the alternative emergency measures and solution.
Why
What
How

## Slide 90: Feasibility Research Consultation Service – Deliverable
Feasibility Consultation Service Deliverable
XXX Data Center
Feasibility Consulting Report
Why
What
How

## Slide 91
DC Planning Process
DC Assessment Models
  Reliability Model
  Energy Efficiency Model
  Economic Model
Site Selection Report
Feasibility Research

## Slide 92
(Multiple choice)In the consulting and planning stage of a new data center, some of the following items are indispensable?
  Site Selection Report
  Feasibility Research
  Operating environment analysis
  Business model analysis
Notes: A B

## Slide 94
HCIE-DCF
1.0
Guobian/Gwx337261
2020/12/3
Lishaofeng/00486775
New