## Slide 1: Overview of Data Center Power Distribution System Planning and Design

## Slide 2
The slides describe the planning and design of the power distribution system in a data center. Some executable standard steps and key decisions made in these steps can simplify and shorten the planning process and improve the planning quality.

## Slide 3
On completion of this course, you will be able to:
  Describe the planning and design process of the data center power distribution system.
  Master the procedure for planning the data center power distribution system.
  Describe the composition of the data center power distribution system.

## Slide 4
Planning and Design Introduction
Planning Composition
Design Composition

## Slide 5: Overview of Power Distribution System Planning and Design
Planning is at the initial phase of the entire data center project and lays a foundation for subsequent work.
In the planning phase, the requirements of the customer (party A) for the new data center are clarified, such as the data center type, total capacity, power density of each cabinet, and data center tier.
In the design phase, specific design is performed based on the input in the planning phase.
Planning
Design
Power distribution system requirement analysis
Power distribution system capacity statistics
Power distribution system solution design
Preliminary design of the power distribution system
Power distribution system construction drawing design
Notes: In the planning phase, the customer's requirements are logically presented in documents using scientific methods and steps. The documents are transferred to the design company. Then the design company performs specific design according to the requirements.

## Slide 6: Planning Procedure
Power distribution system requirement analysis
  Data center tier (requirements for the power distribution system)
  Power density
  Overall capacity planning
  Data center power usage effectiveness (PUE)
Power distribution system capacity statistics
  Based on the previous requirement analysis input, calculate current and future load requirements as the input of the design phase.
Notes: Power distribution system requirement analysis:
  Data center tier: specified by the customer and determines the reliability level of a data center.
  Power density: specified by the customer and determines the power distribution system capacity.
  Capacity planning: The capacity planning of the power distribution system is output based on the customer's IT load capacity. You need to consider how to meet the customer's current and future requirements by reasonable planning.
  PUE: specified by the customer and determines the selection of core devices (mainly the UPS) in the power distribution system. The PUE mainly determines the cooling system.
Power distribution system capacity statistics:
  Collect statistics on the current and future load requirements based on the power density input and power load (mainly the load of the cooling system) of the customer, and use the statistics as the input for the design phase.

## Slide 7: Design Procedure
Power distribution system solution design
  Based on the previous power distribution capacity statistics and requirement analysis, design the power distribution system architecture and the plane of the main equipment, and output the main equipment list and solution description of the power distribution system.
Preliminary design of the power distribution system
  Use the previous power distribution system solution design as the input to design the overall layout of the power distribution system, and output the material list and technical proposal of the power distribution system.
Power distribution system construction drawing design
  Use the preliminary design of the power distribution system as the input to output the bill of quantities (BOQ) and the detailed installation diagram of the power distribution system.
Notes: This course describes the power distribution system solution design, focusing on the power distribution system architecture design, main equipment list, and power distribution solution description.

## Slide 8: Precautions for Planning and Design
Pay attention to the following in the planning and design process:
  Separating solution design and detailed design
    In the early phase of the design process, pay special attention to the following: Ensure that there is consensus on the most important functions of a data center and their costs and do not invest time and efforts in handling detailed design and specifications. In the early phase, properly plan the performance, cost, scale, location, and timing of a data center involved in the project.
  Separating key project specifications and user preferences and restrictions
    During early planning, focus on reaching consensus on specifications such as data center tier and power density, and delay processing user preferences and most of the restrictions to efficiently decide system concepts.
Notes: Separating system concepts and detailed design: Determine system concepts before generating detailed technical specifications, performing detailed design, or discussing various user preferences or requirements. This can bring high efficiency. If performance or cost issues occur after the start of the detailed design, the basic system concept may change, resulting in a large amount of rework and project delay. In the early phase of the design process, pay special attention to the following: Ensure that there is consensus on the most important functions of a data center and their costs and do not invest time and efforts in handling detailed design and specifications. When the system concept is to be determined, high-level decision makers need to determine the macro objectives and properly plan the performance, cost, scale, location, and timing of a data center involved in the project. If stakeholders do not understand the features or costs of the basic design before the detailed design starts, problems may occur in the later phase of the process. This method aims to avoid such problems that are frequently encountered.
Separating key project specifications and user preferences and restrictions: We found that some macro key project specifications are necessary and can support the selection of system concepts. We found that some key specifications, such as power density and expansion plan, were not clearly defined and the quantification method was unclear. During early planning, focus on reaching consensus on specifications and delay processing user preferences and most of the restrictions to efficiently decide system concepts. This ensures that high-level decision makers focus on making the most important decisions, rather than getting stuck in discussions about details.

## Slide 9
Planning and Design Introduction
Planning Composition
  Requirement Analysis
    Data Center Power Distribution System Requirements
  Capacity Statistics
Design Composition

## Slide 10: Overall Function Requirements for the Power Distribution System
Uptime Tier Ⅳ data center (corresponding to TIA Tier 4 data center): must meet the requirements for fault tolerance (one fault) and online maintenance. The power supply and distribution system must meet the requirements for active-active power supply and distribution routes. The two power supply and distribution routes must meet the fault isolation requirements.
Uptime Tier Ⅲ data center (corresponding to TIA Tier 3 data center): must meet the requirements for planned online maintenance. The requirements for active-standby power supply and distribution routes must be met.
Uptime Tier Ⅱ data center: must meet the requirements for redundancy backup.
Uptime Tier Ⅰ data center: only needs to meet the requirements for device running.
Notes: Uptime Tier Ⅳ data center: In terms of fault tolerance, only one fault can be tolerated. In terms of fault isolation, physical fault isolation is required. For example, two routes cannot be routed together, but must be physically isolated. In addition, the distance between the two routes must meet certain requirements, and threats such as fire must be considered.
Uptime Tier Ⅲ data center: Requirement for planned online maintenance must be met. At least active-standby power supply and distribution routes are required. In most cases, both routes are active.
Uptime Tier Ⅱ data center: Requirements for redundancy backup must be met. For example, for the UPS, diesel generators (DG) are redundant, but one single point of failure still occurs on the power supply route.
Uptime Tier Ⅰ data center: There is no redundancy.
The redundancy mentioned here is device redundancy, rather than module redundancy in a modular UPS.

## Slide 11: Specific Requirements for Uptime (1)
Tier Ⅰ: basic data center infrastructure
Basic requirements:
  An Uptime Tier Ⅰ basic data center has non-redundant capacity components and a single non-redundant power distribution route to serve the critical environment. The infrastructure of an Uptime Tier Ⅰ data center includes dedicated space for IT systems, UPSs, cooling equipment, and engine generators.
  Onsite fuel reserve should support 12-hour operation of engine generators.
Example of the power distribution solution
for an Uptime Tier I data center
Notes: Operation effects:
  A data center is prone to interruption during planned and unplanned activities. Misoperations (man-made) on the infrastructure may cause interruption of a data center.
  Unexpected interruptions or failures of any capacity systems, capacity components, or distribution components will affect the critical environment.
  The data center infrastructure must be completely shut down every year to ensure that necessary preventive maintenance and repair work can be performed safely. If an emergency occurs, the infrastructure may need to be shut down more frequently. If maintenance is not performed on a regular basis, the risk of unexpected interruption is greatly increased.

## Slide 12: Specific Requirements for Uptime (2)
Tier Ⅱ: redundant capacity components for the data center infrastructure
Basic requirements:
  An Uptime Tier Ⅱ data center has redundant capacity components and a single non-redundant power distribution route to serve the critical environment. Redundant components include additional UPSs, cooling equipment, and engine generators.
  Onsite fuel reserve should support 12-hour operation of N engine generators.
Example of the power distribution
solution for an Uptime Tier Ⅱ data center
Notes: Operation effects:
  A data center is prone to interruption during planned and unplanned activities. Misoperations (man-made) on the infrastructure may cause interruption of a data center.
  Unexpected capacity component failures may affect the critical environment. Unexpected interruptions or failures of any capacity systems or distribution components will affect the critical environment.
  The data center infrastructure must be completely shut down every year to ensure that necessary preventive maintenance and repair work can be performed safely. If an emergency occurs, the infrastructure may need to be shut down more frequently. If maintenance is not performed on a regular basis, the risk of unexpected interruption is greatly increased.

## Slide 13: Specific Requirements for Uptime (3)
Tier Ⅲ: concurrently maintainable data center infrastructure
Basic requirements:
  Data centers that can be concurrently maintained have redundant capacity components and multiple independent power distribution routes to serve critical systems. At any time, only one power distribution route is required to serve the critical environment.
  All IT devices use dual power supplies and are properly installed to be compatible with the data center architecture topology. If the critical environment does not meet this specification, a transmission device such as a switch must be used.
  Onsite fuel reserve should support 12-hour operation of N engine generators.
Example of the power distribution solution for an Uptime Tier Ⅲ data center
Notes: Operation effects:
  A data center is prone to interruption during planned and unplanned activities. Misoperations (man-made) on the infrastructure components may cause interruption of a data center.
  Unexpected interruptions or failures of any capacity systems will affect the critical environment.
  Unexpected interruptions or failures of any capacity components or power distribution route components may affect the critical environment.
  Planned infrastructure maintenance can be accomplished by using redundant capacity components and power distribution routes to continue safe operation on other devices.
  During maintenance activities, the risk of interruption may increase.

## Slide 14: Specific Requirements for Uptime (4)
Tier Ⅳ: fault tolerant data center infrastructure
Basic requirements:
  A fault tolerant data center has multiple independent systems that are physically isolated to provide redundant capacity components and multiple independent, different, and activated power distribution routes to serve the critical environment at the same time. Redundant capacity components and different power distribution routes should be configured based on the following principle: If any facility is faulty, the "N" capacity provides power and cooling for the critical environment.
  All IT devices use dual power supplies and are properly installed to be compatible with the data center architecture topology. If the critical environment does not meet this specification, a transmission device such as a switch must be used.
  Power distribution routes must be physically isolated (partitioned) to prevent any single event from affecting two systems or power distribution routes at the same time.
  Continuous cooling is required; Onsite fuel reserve should support 12-hour operation of N engine generators.
Notes: Operation effects:
  The data center is not easily interrupted during unplanned activities beyond a single plan.
  The data center is not easily interrupted during planned activities.
  The data center infrastructure can be maintained by using redundant capacity components and power distribution routes to continue safe operation on other devices.
  During maintenance activities where redundant capacity components or power distribution routes are disabled, if the remaining routes are faulty, the risk of interruption in the critical environment increases.
  Using the fire alarm, fire extinguishing, or emergency power-off (EPO) function may interrupt a data center.

## Slide 15: Specific Requirements for Uptime (5)
Example of the power distribution solution for an Uptime Tier Ⅳ data center

## Slide 16: Comparison of Uptime
Data Center Tier | Tier Ⅳ | Tier Ⅲ | Tier Ⅱ | Tier Ⅰ
Overall function requirement | Fault tolerance (one fault), active-active power supply and distribution routes | Planned online maintenance, active-standby power supply and distribution routes | One power supply and distribution route | One power supply and distribution route
Physical isolation requirement | √ | / | / | /
Mains input requirement | / | / | / | /
DG requirement | 2N is recommended, but N+1 can also be used. | N+1 | N+1 | N
Transformer requirement | / | / | / | /
UPS requirement | 2N | N+1 | N+1 | N
Backup time requirement | Meeting DG startup requirements | Meeting DG startup requirements | Meeting DG startup requirements | Meeting DG startup requirements
DG fuel storage requirement | 12 hours | 12 hours | 12 hours | No specific requirements

## Slide 17: Comparison of TIA-942
Data Center Tier | Tier 4 | Tier 3 | Tier 2 | Tier 1
Overall function requirement | Fault tolerance (one fault), active-active power supply and distribution routes | Planned online maintenance, active-standby power supply and distribution routes | One power supply and distribution route | One power supply and distribution route
Physical isolation requirement | √ | / | / | /
Mains input requirement | At least two active-active routes between different substations | One active mains input and one standby mains input (can be from the same substation) | One mains input | One mains input
DG requirement | 2N | N+1 | N | /
Transformer requirement | 2N | N+1 | N | N
UPS requirement | 2N | N+1 | N+1 | N
Backup time requirement | 10 minutes | 10 minutes | 10 minutes | 10 minutes
DG fuel storage requirement | 96 hours | 72 hours | 24 hours | /

## Slide 18
Planning and Design Introduction
Planning Composition
  Requirement Analysis
    Power Distribution System Capacity Planning
  Capacity Statistics
Design Composition

## Slide 19: Capacity Planning Overview (1)
Capacity planning focuses on the capacity of the infrastructure. The objective is to ensure that the power supply capacity is sufficient to support IT loads. To ensure that sufficient capacity is provided when necessary, the maximum predicted load at any point in the life cycle of a data center must be covered during design and planning.
Old method:
  To ensure that there is always enough capacity, the easiest way is to build the infrastructure that can support the maximum predicted load at the beginning. This is a strategy that has been used in the past, but it can result in much waste because in most cases it can lead to over-construction and inefficient use of capacity.
New method: The phased capacity expansion plan is used to reduce waste. Phased capacity expansion has important advantages:
  Less capacity is wasted during the transition period.
  Uncertainty of growth is reduced.
Notes: Old method: Over-construction leads to waste.
Such waste includes capital costs for idle equipment and operating costs for idle capacity. During the life cycle of a data center, the cost of supplying power to unnecessary capacity components and the cost of maintaining and repairing them may be huge.
The idle capacity can be generated in either of the following ways:
  If the IT load is small at the beginning and increases with time, the system will be over-constructed during the transition period.
  If the IT load never reaches the predicted level, the system is over-constructed in the entire life cycle. Most data centers will never reach their predicted full capacity. In practice, data centers typically operate with less than half of the capacity.

## Slide 20: Capacity Planning Overview (2)
IT load capacity curve: It is provided by the customer's IT department and shows the IT capacity planning of the entire data center lifecycle.
Power distribution system capacity curve: The IT load capacity curve is used as the input and capacity is expanded by phase to ensure that the power supply capacity is sufficient to support IT loads.
IT load capacity curve
Power distribution system capacity curve
Input
Output

## Slide 21: IT Load Curve (1)
Most data center plans are vague because they do not incorporate the evolving technology feature of IT devices. One way to solve the uncertainty problem is to set reasonable maximum and minimum values that can be expected in the life cycle of a data center to provide support for the prediction. Once the maximum and minimum estimated values of the final load are determined, you only need to add the initial load and transition time to predict the IT load growth.
  Maximum final load: predicted maximum IT load.
  Minimum final load: predicted minimum IT load.
  Initial load: IT load that is initially installed.
  Transition time: time required from the initial load to the final load. Generally, the life cycle of a data center is 10 years.
Notes: Most data center plans are vague because they do not incorporate the evolving technology feature of IT devices. In addition, the business requirements that drive data center design and/or service requirements are difficult to be understood in advance. The reliability of the prediction decreases as the IT load in a farther future is predicted. Any model with forward-looking capacity requirements needs to take into account information about the quality (certainty) of the predictive activity itself. One way to solve the uncertainty problem is to set reasonable maximum and minimum values that can be expected in the life cycle of a data center to provide support for the prediction. The preceding figure shows the concepts of the minimum and maximum values of the final load. Generally, the life cycle of a data center is 10 years. Once the maximum and minimum estimated values of the final load are determined, you only need to add the initial load and transition time to predict the IT load growth.
The model shows the predicted maximum and minimum values of the final load, but does not explicitly predict the actual value of the final load. Any description of the actual value of the final load is just a guess in most cases. The actual value of the final load of a particular device generally depends on multiple variables, some of which may not be predicted by the planner or even may be unknown.

## Slide 22: IT Load Curve (2)
A more effective planning method of this growth model is to identify the upper and lower limits of the final load, which can be more reliable and consistent than a single predicted load level.
When the predicted maximum and minimum values of the load are identified, the intelligence of the model is increased and the system capacity planning can cover the uncertainty of growth, which provides a simple strategy to minimize the risk of over-construction and reduce the total cost of ownership.
Notes: During planning, users tend to adopt the predicted maximum load, because the possible maximum load was always the "safe" value used during the initial deployment of the design system, and planners have got used to that way of thinking. The predicted minimum load may seem superfluous, but it is the key to achieving the considerable cost-effectiveness of the growth model.

## Slide 23: Power Distribution System Capacity Curve (1)
Capacity expansion scale: incremental scale of the physical infrastructure system (capacity expansion delay).
Security tolerance: extra capacity to cope with unexpected situations (such as unexpected increase of IT loads or unexpected consumption of system capacity).
Notes: Capacity expansion scale is an attribute of system capacity planning, not an attribute of the IT load curve. It is decided at the later stage of the planning process, taking into account the scalability of the selected system architecture.
Security tolerance refers to the "extra" infrastructure capacity required to cope with unexpected changes, which may be an increase in the power demand for IT loads (for example, adding servers without authorization) or a decrease in the capacity provided by the power supply and cooling infrastructure (for example, cooling capacity decrease caused by cooling pipe blockage).

## Slide 24: Power Distribution System Capacity Curve (2)
Differences between the IT load curve and system capacity planning
  The model provides a common language and framework to help users understand IT load requirements and help physical infrastructure designers plan a system with sufficient power and cooling capacity to meet the load requirements. They are interdependent.
  First part of the model: The IT load curve is provided by the user as an input to the planning process.
  Second part of the model: The system capacity planning is provided by the planning process as the output to the user to define the deployment of the power supply infrastructure (including the step-by-step capacity expansion phase) to support the IT load curve of the user.

## Slide 25: Power Distribution System Capacity Curve (3)
Therefore, for a specific project, the model development is divided into two parts:
  First, establish an IT load curve. The IT load curve consists of parameters 1 to 4 of the model. It is created based on the understanding of enterprise service requirements at the early stage of the planning process. The key to this step is to get the participants in the planning process to agree on the predicted IT load.
  Second, the system capacity planning is established to support the IT load curve. The system capacity planning is represented by (capacity expansion scale and security tolerance) of the model. The system capacity planning is performed at the early stage of the planning process to roughly estimate the capacity expansion scale.

## Slide 26: Benefits of Phased Capacity Expansion
Phased capacity expansion refers to a phased capacity expansion policy for system capacity planning during the IT load transition period.
  If phased capacity expansion is used, the power supply and cooling capacity increases with IT loads, avoiding unnecessary capital and operation costs (especially energy costs).
  If the future load is uncertain, a re-evaluation point can be provided at each phase. At this point, a decision can be made to delay or reduce the process of the next phase or stop the capacity expansion completely.
Phased capacity expansion allows you to give up capacity planning in any phase when the future capacity is clear.
System capacity planning
Original planning
Modified planning
Actual final load reached in advance
Minimum predicted load
Maximum predicted load
Capacity expansion and growth have been stopped.
Time
Transition time
Initial load
The uncertain future requirements can be evaluated more frequently if the interval of phased capacity expansion is shorter.
System capacity planning
Original planning
Modified planning
Maximum predicted load
Actual final load reached in advance
Minimum predicted load
Capacity expansion and growth have been stopped.
Time
Transition time
Initial load
Phased evaluation
Notes: Although these concepts are not new to many applications in daily life, the legacy power supply and cooling architecture that cannot be expanded in a data center has dominated the initial capacity expansion of the entire facility for decades. However, recent developments in scalable modular system architecture have enabled designers to take advantage of the important benefits brought by phased deployment.
There are three factors that make phased capacity expansion particularly attractive:
  Energy has become a major expense. Electricity bills provide a powerful incentive to avoid overcapacity. Incentives for "green buildings" and "demand-side management" programs that reward efficient operations provide more incentives for running streamlined data centers. A data center with "reasonable planning" (power supply and cooling capacity keeping pace with the IT load growth) is more efficient than a data center with too much idle capacity.

## Slide 27
Notes:   Most data centers never expand to their predicted largest scales. Research shows that the final load of most data centers is far lower than the maximum load predicted during planning. Phased capacity expansion reduces the risks caused by waste of installation resources. This is the biggest advantage of phased capacity expansion for most data centers.
  Idle capacity causes unnecessary maintenance costs. Even if the capacity is idle, the installed equipment must be maintained and repaired. By installing only the capacity equipment required to support the current load, you can save a large number of maintenance costs, because no maintenance costs will be incurred for unavailable equipment.

## Slide 28: Technical Support for Phased Capacity Expansion
Developments in scalable modular system architecture have enabled designers to take advantage of the important benefits brought by phased deployment.
The entire data center is divided into scalable (modular) and non-scalable components.
Scalable components can be expanded by phase to reduce the risk of excessive construction.
Initial load
Capacity expansion in phase 1
Row 1
Initial load
Maximum final load
Non-scalable components
The capacity in the early stage meets the maximum final load.
Equipment room size
Capacity expansion in phase 2
Row 2
Row 3
Row 4
Row 5
Cable inlet
Switchgear
Heat dissipation devices (such as chillers)
Deployment of scalable and non-scalable components during capacity planning
Notes: Non-scalable components are installed at the beginning to accommodate the predicted maximum load (the maximum final load value) in the data center life cycle. Non-scalable components include the physical equipment room size, electrical cable inlet capacity, and pre-existing in-room air conditioners. These "rigid" capacity limits can seriously impact time, availability, and cost.
Scalable components are installed at the beginning to support loads lower than the maximum value (enough to support the initial load for a period of time), and then are gradually increased as time goes by according to the phased capacity expansion planning. Scalable components include racks, rack-level power protection and distribution equipment, and rack-level cooling equipment.

## Slide 29: Application of Phased Capacity Expansion – Modular Data Centers
Notes: The left part of the figure lists the subsystems of the data center. Gray blocks indicate devices. If all device blocks exist, the data center uses the maximum configuration. However, the device blocks are deployed from left to right to gradually expand the data center to meet the increasing IT load requirements. The capacity of all subsystems listed on the left must match the given IT capacity (kW). The gray modules of the subsystem must be added in a way that meets the capacity expansion requirements of the data center. The figure also provides the association between different subsystem modules. As shown in the figure, in-row air conditioners are deployed by area. Every three in-row air conditioners have one backup device to form N+1 redundancy. One humidifier is deployed for every twelve in-row air conditioners, and one humidifier is associated with one equipment room.
As shown in the preceding figure, the preceding subsystems are associated with each other in the unit of 60 kW. These associated subsystems form an area with a certain IT capacity as the core deployment module of the architecture. In this architecture, the area includes the cabinet, rack-mounted PDU, terminal PDF, UPS, in-row air conditioner, and hot aisle airflow containment system.
As discussed earlier, IT area-based deployment is not effective for some subsystems. In the architecture shown in the figure, the humidifier, liquid distribution unit (LDU), chilled water pump, and lighting are associated and matched to support three IT areas at the same time. In this architecture, these subsystems and three IT areas form an equipment room module. The boundary of an equipment room can be a physical wall or a virtual wall, which usually refers to a partition in a large equipment room.

## Slide 30
Notes: In a data center, there are also some centralized subsystems that are optimally deployed in units of facilities. As shown in the figure, these subsystems include the chillers, free cooling heat exchangers, cooling towers, generators, and switches. Some subsystems, such as generators, are not modular, while others, such as chillers, are modular.
In this example, the chillers work in N+1 redundancy mode, and each module supports 4.5 areas. In this example, modular chillers deployed in a centralized manner do not need to correspond to areas or equipment rooms. In this architecture, the two chillers on the left must be installed at the initial stage to provide N+1 redundancy. Install the third chiller after the fifth area is added. The blue line between two chillers in the upper row indicates that the two chillers are connected to the same main pipe. Therefore, the N+1 chillers in the lower row are redundant devices for the two chillers. At the beginning, it seems that small chillers can provide high scalability, which is consistent with area deployment. However, if the chillers are divided into small modules, the cost is high and the complexity increases. In this architecture, a chiller can supply cooling to a large area. To save energy, you need to select a model with an inverter compressor.

## Slide 31
Planning and Design Introduction
Planning Composition
  Requirement Analysis
    Data Center PUE
  Capacity Statistics
Design Composition

## Slide 32: PUE
PUE =
PUE is proposed by The Green Grid and has become a core indicator for evaluating the efficiency of the physical infrastructure layer (equipment room) of a data center.
Power input
Heat output
Chiller 23%
Humidifier 3%
CRAC/CRAH 15%
IT device 47%
PUE = 2.13
PDU 3%
UPS 6%
Lighting and auxiliary equipment 2%
Switchgear/Generator 1%
Indoor data center heat
Total energy input to a data center
Energy consumed by IT loads
Notes: The PUE value is greater than 1. Currently, the PUE value of a modular data center ranges from 1.1 to 1.8 (using cold and hot aisle containment, in-row air conditioners, and modular UPSs). The PUE value of a traditional data center ranges from 1.8 to 3.5 (using in-room air conditioners, without cold and hot aisle containment).
PUE determination is important for device selection and data center architecture. It is mainly reflected in the cooling solution, for example, whether to use air-cooled direct expansion air conditioners, chilled water air conditioners, or cooling devices with the indirect evaporation function. For example, the PUE of a data center using common air-cooled in-row air conditioners ranges from 1.5 to 1.7; the PUE of a data center using chilled water in-row air conditioners can be about 1.3; the PUE of a data center using indirect evaporative cooling devices can be less than 1.2.
Modular UPSs and PDUs are used to reduce power distribution loss.

## Slide 33: Methods of Reducing the PUE of a Data Center (1)
There are three methods to improve the data center efficiency:
  Improve the internal design of the data center facility (DCF) equipment to reduce the energy consumption during operation.
  The planning of DCF components better matches the actual IT load (moderate planning) to improve the operating efficiency of components.
  Develop new technologies to reduce the power required to provide the data center physical infrastructure (DCPI) support functions, such as free cooling.
Power input to the
data center
Requiring less power
Reducing loss here
IT power
supply
Support area power supply
Data center
UPS
PDU
Cabling
Switch
Cooling
Lighting
Firefighting
Security
Generator
Switchgear
Power input to IT devices
Unchanged IT load
IT devices
Reducing loss here
DCPI
IT

## Slide 34: Methods of Reducing the PUE of a Data Center (2)
The planning of DCF components better matches the actual IT load (moderate planning) to improve the operating efficiency of components. This provides the maximum and most direct opportunity for improving the efficiency of a data center, because the operating efficiency of a device is the highest when the load rate is reasonable.
Therefore, you need to:
  Properly plan the system capacity.
  Select modular UPSs and rack-mounted PDUs.

## Slide 35
Specify the requirements for the power distribution system based on the data center tier.
The capacity needs to be expanded by phase. Different components need to be expanded in different modes. For example, a data center is constructed in three phases, and eight sets of high-voltage (HV) DG systems are required to work in 7+1 mode. In the initial construction, 2+1 DGs can be installed to meet the requirements of phase 1. However, all high-voltage (HV) cabinets corresponding to the DGs need to be installed, and ports need to be reserved for installing DGs in batches in the future. Other devices, such as modular UPSs and in-row air conditioners, should be expanded gradually based on load requirements.
Proper planning of infrastructure capacity improves the operating efficiency of components and provides the maximum and most direct opportunity for reducing the PUE of a data center.

## Slide 36
Planning and Design Introduction
Planning Composition
  Requirement Analysis
  Capacity Statistics
Design Composition

## Slide 37: Capacity Calculation Principles (1)
To estimate the power requirements of a data center, you need to understand the power required by the cooling system, UPS system, and key IT loads.
  Key load: refers to all IT hardware components that constitute the IT service architecture, including servers, routers, computers, storage devices, communications devices, security systems, fire extinguishing systems, and monitoring systems. The future load must be considered during estimation.
  UPS system: The efficiency loss factor of the UPS system and the extra power required for battery charging need to be considered.
  Lighting facility load: includes all lighting facilities in data center buildings and is a function of the floor area of a data center. There is a good empirical formula for this type of load: about 21.5 W per square meter.
  Cooling system: The cooling system capacity needs to be calculated additionally, but can also be obtained by estimation. The efficiency of a chilled water system is usually higher, and the power consumption is usually 70% of the total peak load supported. A direct expansion system requires approximately 100% of the total peak load supported.
Notes: Although the power requirements of these elements may differ greatly from each other, if the power requirements of the planned IT loads are determined, the power requirements of these elements may be accurately estimated using a simple method. In addition to estimating the capacity of the power lines, these elements can also be used to estimate the power output capacity of the standby generator system if the load of a data center requires a standby generator system.
Why does the future load need to be considered? Because IT devices in data centers are constantly updated, we must fully estimate the capacity of power lines that supply power to DCPI components so that the known initial load and future load can be supported. After the future load is estimated, add it to the calculated basic load to obtain the key load of the power supply in the unit of kW.
The UPS efficiency varies with the load rate. Generally, the UPS efficiency of 0.9 is considered. Battery charging does not continuously consume power. When a battery is fully charged, its charge load can be ignored. However, after the battery is partially or completely discharged, the charge power can reach 15% to 20% of the rated power of the UPS. Although such loads are rare, they must be included in the estimation of generator and line inlet capacity.

## Slide 38: Capacity Calculation Principles (2)
After the total power capacity in the unit of kW is estimated, two key calculations can be performed: First, estimate the capacity of the power lines required for supplying power to a data center. Second, estimate the capacity of all standby generators required for achieving the expected availability.
  Determine the capacity of the power lines.
    Current (A) = (Power (kW) x 1000)/(Voltage (V) x 1.73). The voltage is the line voltage. The power needs to be multiplied by a coefficient ranging from 1.2 to 1.25 according to the corresponding specifications.
  Determine the generator capacity.
    The generator capacity is in the unit of kVA, but the preceding capacity is in the unit of kW. Therefore, the power factor needs to be considered. Generally, the power factor of 0.8 is used. In addition, the load characteristics and startup voltage of the chiller or UPS need to be considered.

## Slide 39: Key Load Capacity Statistics (1)
Principle
  Statistics are collected based on the data center layout, that is, based on different functional areas, such as the IT room, access equipment room, operation room, and fire control room.
Input
  Cabinet power density
  Number of cabinets
  Power requirements of fire extinguishing, access control, and monitoring devices

## Slide 40: Example of Key Load Capacity Statistics
Functional Room | Device Name | Rated Power (kW) | Quantity | Power Factor | Required Power |  | 
 |  |  |  |  | Active Power (kW) | Reactive Power (kVAR) | Apparent Power (kVA)
IT room 1 | Server cabinet | 7 | 200 | 0.9 |  |  | 
 | Network cabinet | 3 | 20 | 0.9 |  |  | 
 | Test cabinet | 4 | 5 | 0.9 |  |  | 
IT room 2 | Server cabinet | 10 | 150 | 0.9 |  |  | 
 | Network cabinet | 3 | 15 | 0.9 |  |  | 
 | Test cabinet | 4 | 5 | 0.9 |  |  | 
Operation room | PC in the operation room | 0.3 | 16 | 0.8 |  |  | 
 | 61-inch screen | 1.2 | 1 | 0.8 |  |  | 
 | Monitoring device | 7 | 1 | 0.9 |  |  | 
Fire control room | Fire extinguishing device | 5 | 1 | 0.9 |  |  | 
Key load statistics of a data center
Notes: In the industry, the IT power factor of 0.9 is usually used for estimation.

## Slide 41: Questions
Based on the following table, customers may ask the following questions:
  Is the server cabinet power 7 kW the maximum power, minimum power, or average power?
  If the peak power of a cabinet exceeds 7 kW, can the cabinet work properly?
  If the power consumption of a cabinet is lower than 7 kW, can adjacent cabinets use the remaining power of the cabinet?
  How to meet the requirement of adding extra services in the future?
Functional Room | Device Name | Rated Power (kW) | Quantity | Power Factor | Required Power |  | 
 |  |  |  |  | Active Power (kW) | Reactive Power (kVAR) | Apparent Power (kVA)
IT room 1 | Server cabinet | 7 | 200 | 0.9 |  |  | 
 | Network cabinet | 3 | 20 | 0.9 |  |  | 
 | Test cabinet | 4 | 5 | 0.9 |  |  | 
Notes: This table cannot answer the preceding questions. A more detailed table is required to convince customers that the current plan can meet the actual requirements.

## Slide 42: IT Load Capacity Statistics (1)
Layers of the entire data center:
  Data center facilities, consisting of one or more IT rooms
  IT room, consisting of one or more IT areas
  IT area, consisting of one or more IT cabinets
  IT cabinet
Since some attributes of a data center are affected by the power density specifications of each layer, the power density specifications of the four layers must be specified to control the entire design and predict the performance of the data center.
Although the power density specifications of each part can be "accumulated" into a single facility-level power density value, the single power density value obtained in this manner is not enough to control the entire design and obtain a predictable result.
Notes: The power density varies with IT cabinets, IT areas, and equipment rooms. This difference exists between cabinets or between equipment rooms, and the power density also varies with time. Because some IT devices are added or removed from time to time and the workloads of these IT devices are different, the power consumed by these IT devices is also different. The operating power of each cabinet is different, and the power of the same cabinet varies in different periods. From this point of view, trying to define power density also seems to be futile. However, considering that the objective of defining the power density is to determine a data center design that can support an IT device cluster, we can determine many important statistical parameters of the device cluster, and these statistical parameters are sufficient to form power density specifications that do not vary with the power density difference.

## Slide 43: IT Load Capacity Statistics (2)
Determining specifications
Specifications | Definition | Usage Method
Number of units | Number of cabinets in an IT area, number of IT areas in an equipment room, or number of equipment rooms | Convert the values of each unit requiring power supply to a total value (each cabinet, each IT area, and each equipment room).
Designed target average power of each unit (kW) | Average expected load power (average power or rated power) of each unit | Determine the capacity of the power distribution system at each layer (IT area, equipment room, and facility).
Peak power of each unit (kW) | Maximum expected power of a unit | Determine the requirements for the power distribution system.
Uncertainty of unit power (%) | The expected uncertainty of the actual power is quantified compared to the designed target average power. | Determine the required reserved space to ensure that the low-density power deployment does not cause the power supply capacity to be wasted, which increases the cost.
Notes: The number of units and the designed target average power of each unit are necessary information for determining the power density specifications. The peak power and the uncertainty of unit power are new concepts introduced here. These are necessary because the designed target average power does not provide the necessary information to determine the power distribution system, and does not provide sufficient information to determine the energy efficiency calculation point.
The relationship between the designed target average power of each unit and the peak power of each unit is as follows: As long as the average power of a unit does not exceed the target average power, the peak power of the unit can be reached. For example, in an IT area where the average power is 5 kW/rack and the peak power is 10 kW/rack, if the average power of the area is 5 kW/rack or lower, the power of one or more cabinets can reach 10 kW. In this case, the actual power of other cabinets must be lower than 5 kW, for example, 3 kW or 3.5 kW.
Uncertainty of unit power: If the actual power of installed equipment is lower than the target power but the actual installation space is all occupied, the power distribution and cooling capacity will be wasted. In this case, if certain space is reserved during planning, more IT loads can be installed. This ensures that the utilization of the infrastructure capacity is maximized during low-density installation.

## Slide 44: Example 1 - Small-sized Data Center (1)
A small server room with only one IT room and one IT area is used as an example. In this case, the specification layer is the equipment room, which is also the IT area. The equipment room contains a group of IT cabinets.
Number of cabinets
Designed average power density
of each cabinet
Peak power of the cabinet
Uncertainty of cabinet power
Rated system power
Rated power of each cabinet
Rated peak power of each cabinet
Expected unused space
Number of reserved cabinets
Space specifications
12
4 kW
8 kW
15%
48 kW
4 kW
8 kW
15%
2
Power density
specifications
Equipment room
performance
specifications
Notes: The power density in the specifications can be determined by the following procedure:
  Determine the number of cabinets based on IT requirements.
  The target average power of each cabinet is determined by the specifications of the IT cabinet supplier or by the typical designed average value of the application. In this example, the typical value of an enterprise server room (4 kW/cabinet) is selected.
  Select the peak power by setting the maximum expected or allowed cabinet power. In this example, the maximum capacity is 8 kW. This value is mainly determined by the rPDU provided by the cabinet supplier to support the cooling capacity and power supply capacity.
  Estimate the uncertainty of the cabinet power by considering different IT deployment solutions or selecting the typical designed value of the application. In this example, the expected deployment power density is set to 15% of the designed target average power (4 kW).

## Slide 45: Example 1 - Small-sized Data Center (2)
The key point here is not that the plan can accurately reflect the detailed IT plan of each cabinet (because the IT plan of each device cannot be obtained in advance), but that the plan can ensure that the performance of a data center is known and predictable.
In this example,
  The specifications clearly define design that supports a cabinet group containing up to 12 cabinets.
  In the cabinet group, the designed average power is 4 kW, and the peak power of each cabinet is less than or equal to 8 kW.
  To ensure that the peak power is not exceeded, a pre-deployment IT policy can be formulated for the data center. According to the policy, the maximum power of each cabinet is 8 kW. When the load increases, the power must be allocated to each cabinet.
  If the actual IT power density is less than 15% of the designed average value (4 kW), the extra reserved space can ensure that all available power supply and cooling capacity can be used.
Notes: If the traditional method is used to describe the IT load of the equipment room, these issues cannot be explained.

## Slide 46: Example 2 - Large-sized Data Center (1)
In this data center example, the data center adopts the following layered structure:
  The data center facilities consist of
  Four IT rooms, each of which consists of
  Six IT areas, each of which consists of
  16 IT cabinets
The procedure is as follows:
  Determine the number of cabinets in each IT area and set the cabinet power.
  Determine the number of IT areas in each equipment room and set the IT area power.
  Determine the number of equipment rooms and set the equipment room power.
  Set specifications for facilities, IT areas, and equipment room space.
  Integrate the overall specifications and verify the specifications based on the design constraints. Continuously adjust the design and repeat the procedure until the design meets the requirements.

## Slide 47: Example 2 - Large-sized Data Center (2)
Number of units
Designed average
power density of each unit
Peak power of each unit
Power uncertainty of each unit
Rated system power
Rated power of each unit
Rated peak power of each unit
Expected unused space
Reserved space of each unit
Space specifications
4
480 kW
480 kW
/
1920 kW/facility
480 kW/equipment room
480 kW/equipment room
/
/
6
80 kW
80 kW
/
480 kW/equipment room
80 kW
80 kW
/
/
16
5 kW
10 kW
15%
80 kW/IT area
5 kW/cabinet
10 kW/cabinet
15%
3 cabinets
Facility
Equipment room
Equipment room
IT area
IT area
cabinet
Power density
specifications
Equipment room
performance
specifications
Notes: Note: In this case, only the IT cabinet unit involves uncertainty. Three cabinet positions are reserved. In actual applications, one or two IT area positions can be reserved (if necessary) to plan the new IT area without interrupting the existing IT areas and to fully utilize the power supply and cooling of the equipment room when the average power of deployed cabinets is lower than 5 kW.
This table is more complex than the previous example of a single equipment room because it clearly records the space reserved for dealing with the uncertainty of power density. Users do not need to enter the IT area or equipment room because the uncertainty at the IT layer of a single cabinet has been predicted and considered. These layers are formed by accumulating lower layers. However, during design, users may reserve space to deal with uncertainty at different layers. Users can reserve extra cabinet positions in the IT area, reserve more IT area positions in the equipment room, reserve extra equipment room space in the facilities, or combine the three methods to reserve space for dealing with the uncertainty of power density. Which method of reserving space is most preferred depends on the geometric shape of the equipment room or other factors. This table records the overall space requirements so that users can reserve space using any combination of additional cabinets, IT areas, or equipment rooms.

## Slide 48: Example 2 - Large-sized Data Center (3)
For simplicity, this example assumes that the specifications of the IT area in all equipment rooms are the same, and the changes only exist at the cabinet layer.
The table is concise, but contains a large amount of design information. The table consists of three columns. The left column indicates the equipment room composition of the facility, the middle column indicates the IT area composition of the equipment room, and the right column indicates the cabinet composition of the IT area. The table defines the attributes of the 2 MW (IT load) data center example as follows:
  An IT area consists of 16 IT cabinets and three reserved cabinet positions.
  The designed average power of each cabinet is 5 kW.
  If the IT area power of all 16 cabinets does not exceed 80 kW, the allowable peak power of any cabinet is 10 kW.
  Three cabinet positions are reserved in each IT area. If the deployed average power is less than 5 kW per cabinet, the power supply and cooling in the IT areas can be fully utilized.

## Slide 49: Capacity Statistics Example (1)
Item | Required Data | Calculation | Total (kW)
Power Requirement – Electricity |  |  | 
Key load capacity | Rated power of each IT device (initial) |  | #1_________kW
 | Other load capacity (including fire extinguishing, security, and monitoring devices) |  | #2_________kW
 | Rated power of each future IT load |  | #3_________kW
Attenuation coefficient | Total power decrease of the key load in the stable state | (#1 + #2 + #3) x 1.05 | #4_________kW
UPS power loss and battery charge | Actual load + Future load (kW) | (#1 + #2 + #3) x 0.3 | #5_________kW
Lighting facilities | Total floor area related to the data center | 0.0215 x Floor area (m2) | #6_________kW
Total power required for power supply | Sum of #4, #5, and #6 | #4 + #5 + #6 | #7_________kW
Data center power requirement estimation and calculation table
Notes: 0.3 = 0.2 + 0.1, including battery charge loss and UPS efficiency

## Slide 50: Capacity Statistics Example (2)
Item | Required Data | Calculation | Total (kW)
Power Requirement – Cooling |  |  | 
Total power required for cooling | Sum of the values in #7 | Chiller system: #7 x 0.7 DX system: #7 x 1.0 | #8_________kW
Total Power Consumption |  |  | 
Total power required for power supply and cooling | Sum of #7 and #8 | #7 + #8 | #9_________kW
Estimating the Capacity of Power Lines |  |  | 
Capacity meeting the requirements of various standards | Sum of the values in #9 | #9 x 1.25 | #10_________kW
Three-phase AC voltage provided at the entry of the lines | AC voltage |  | #11_________kW
Power capacity to be obtained from the power supply company (in amperes) | Sum in #10 and AC voltage in #11 | (#10 x 1000)/(#11 x 1.73) | _________A
Data center power requirement estimation and calculation table

## Slide 51: Capacity Statistics Example (3)
Item | Required Data | Calculation | Total (kW)
Estimating the Capacity of the Standby Generator |  |  | 
Key load that requires a standby generator | Sum of the values in #7 | #7 x 1.3 | #12_________kW
Cooling load that requires a standby generator | Sum of the values in #8 | #8 x 1.5 | #13_________kW
Required generator capacity | Sum of #12 and #13 | #12 + #13 | _________kW
Data center power requirement estimation and calculation table

## Slide 52
Capacity statistics are collected by area (room), such as IT load, cooling load, lighting load, and fire extinguishing load.
When collecting statistics on key loads (IT loads), you need to collect statistics on the loads at four layers: cabinet, area, equipment room, and data center facility. The number of units, average power, maximum power, and space reserved for uncertainty must be specified.
Finally, the active power, reactive power, and apparent power required by a data center are obtained by accumulating all loads and are used as the input for the selection of the DG and mains.

## Slide 53
Planning and Design Introduction
Planning Composition
Design Composition

## Slide 54: Design Overview
Design the power distribution system based on the plan input in the early stage.
The design covers the 35 kV and lower power supply and distribution systems, including the 35 kV/10 kV/400 V transformer, 35 kV/10 kV/400 V DG, HV or low-voltage (LV) PDF, bus, UPS, and ATS.
Power supply and distribution system (HV DG)
Notes: The power supply and distribution system of a data center provides stable and reliable power for all devices in the equipment room, including subsystems of HV power distribution, LV power distribution, DG set, UPS, HVDC, battery, grounding, and server power supply.
  HV power distribution system: introduces the HV mains power supply (such as 6 kV/10 kV/35 kV) into the transformer, which is then converted into LV mains to supply power to the LV power distribution equipment.
  DG set system: quickly starts to provide backup power for the downstream LV equipment in case of mains failures.
  LV power distribution system: introduces the LV mains power from the transformer and distributes the mains power to the UPS PDF, DC, and power PDFs. Then, the power is distributed to IT loads, cooling loads, and other auxiliary devices based on load requirements and standards.
  UPS and HVDC: purify and back up electric energy, and provide pure and reliable power protection for IT loads.
  Battery: stores energy based on chemical principles and ensures that the UPS and HVDC supply power to IT loads without interruption.
  Grounding system: provides reliable grounding for the system to ensure the safe operation of the equipment and personal safety.
  Server power supply: converts AC or DC power into 12 V power to provide stable power for internal components (such as CPUs, hard disks, and memory) of the server.

## Slide 55: Subsystem Design
HV power distribution system
LV power distribution system
DG set system
UPS
Surge protection and grounding system
Data center power supply and distribution system
Notes: HV power distribution system: In China, the voltage of HV power distribution systems is generally 35 kV or lower. If the voltage is higher than 35 kV, the power grid is greatly affected. Generally, a professional power supply company provides systems of more than 35 kV. The system includes: HV switches, HV power distribution facilities (if any), HV DG sets (if any), and transformers. The design includes load analysis, determination of the number of inlet circuits and voltage level, power supply topology design, and HV switchgear and transformer configuration.
LV power distribution system: LV power supply topology design (single-route or dual-route power supply solution), and selection and design of various LV switches, conductors, and PDFs
DG set: type (HV or LV), operating mode (single or parallel), operating condition (emergency or continuous), fuel tank capacity, controller, parallel cabinet, and ATS cabinet
UPS: type (modular or tower-mounted), operating mode (parallel, single, or dual-bus), battery backup time, and battery switch selection
Surge protection and grounding system: includes the surge protection system and grounding system, involving the power surge protection design, signal system surge protection design, grounding mode, equipotential bonding mode, and grounding device design.
This course describes the design of the UPS, LV power distribution system, and DG system.

## Slide 56
Planning and Design Introduction
Planning Composition
  Requirement Analysis
    Data Center Power Distribution System Requirements
    Power Distribution System Capacity Planning
    Data Center PUE
  Capacity Statistics
Design Composition

## Slide 57
(short-answer question) What is the purpose of reserving 15% cabinet space for power uncertainty during planning?
Notes: Answer:
  1. If the actual power density of the installed equipment does not reach the designed value, the standby cabinet can be used to install IT devices to fully use the facility capacity.

## Slide 59
V5R2
V1R1
2019.01.25
Update
Chenkaifeng/cwx377854
2020.9.31
Lishaofeng/486775
New
2019.01.25
Update
2019.01.25
Update
2019.01.25
Update
2019.01.25
Update