## Slide 1: Data Center UPS System Planning

## Slide 2
The slides describe the data center UPS system planning, including requirement analysis, typical configuration solutions, capacity calculation, device selection, and battery configuration.

## Slide 3
On completion of this course, you will be able to:
  Master UPS system requirement analysis.
  Be familiar with common UPS configuration solutions.
  Master the way to calculate the UPS system capacity.
  Understand the UPS system battery configuration.

## Slide 4
System Composition
Planning Preparation
Planning Method

## Slide 5: System Composition (1)
The static uninterruptible power system (UPS) consists of UPS, battery strings, battery racks, battery switches, battery switch boxes, parallel components, communication components, and connecting cables.
UPS
  By the technology, UPS are classified into transformer-based UPSs and transformerless UPS (modular UPS are transformerless UPS).
  By the architecture, UPS are classified into offline UPS, online interactive UPS, and double-conversion UPS. Only double-conversion UPS can meet all the core requirements of data center customers. Double-conversion UPS are most widely used in data centers.
  By the capacity, UPS are classified into small-capacity UPS (< 20 kVA), medium-capacity UPS (20 kVA–200 kVA), and large-capacity UPS (> 200 kVA). The UPS used in data centers are mainly medium-capacity and large-capacity UPS.
Notes: When selecting UPS for data centers, customers first consider the UPS technology classification (transformer-based UPS and transformerless UPS). Currently, mainstream vendors in the industry are shifting to production of transformerless UPS.
Note:
  The UPS and the inverter cannot be configured concurrently in the same data center. If a data center requires multiple AC power sources (UPS and inverter), it is advised to configure either the UPS or inverter based on the total power. Do not select the UPS power supply for some devices and the inverter power supply for other devices.
  Use UPS from the same vendor for one data center in one solution. All product lines must reach consensus with each other during the preparation and final review of the same bidding document. Do not use UPS from various vendors for all devices.

## Slide 6: System Composition (2)
Battery string
  The battery string serves as the backup power supply. When the mains supply is faulty, the battery string supplies power to the load.
Parallel components
  Parallel components include parallel cards and parallel cables. When multiple UPS are connected in parallel, a parallel card is required for each UPS to implement parallel control. Parallel UPS communicate with each other over the parallel cards.
Notes: Parallel components: UPS exchange information through parallel cables that are connected in a closed loop. The closed-loop connection provides redundancy for cable connections (there are communication cables between independent UPS). This connection method allows the online access and exit of one UPS. Each UPS provides a controller to communicate with other UPS, which ensures proper running of the entire parallel system.

## Slide 7: System Composition (2)
Communication components
  Communication components are used to monitor the UPS and implement the communication of monitoring data with remote platforms. Huawei UPS communication components include Simple Network Management Protocol (SNMP) cards, Modbus cards, and dry contact cards. Configure them based on the actual situation.
Load bus synchronization controller
  The load bus synchronization controller is used in a dual-bus UPS system to ensure the synchronization of two UPS output systems.
Notes: The load bus synchronization controller is used in a dual-bus UPS system to ensure the synchronization of two UPS output systems. It works as follows: Any parallel UPS system is set as the master UPS. The system monitors the UPS output frequency and phase on the two buses at the same time. Once they exceed the synchronization tracking range, the synchronization controller is activated. The internal control system continues to track the mains for the master UPS. The UPS on the other bus tracks and controls the slave UPS through the synchronization controller. In this way, the two systems are synchronized.

## Slide 8
System Composition
Planning Preparation
Planning Method

## Slide 9: Planning Preparation - Requirement Input
Requirement input
IT equipment power
Backup time
Local altitude
Data center level
Notes: The requirement input includes the following four points:
  The data center level determines the UPS configuration solution.
  The IT equipment power determines the capacity of a single UPS and UPS quantity.
  The backup time determines the capacity of a single battery string and the number of battery strings.
  The local altitude affects the UPS output and determines whether it should be derated. If the altitude increases, the pressure decreases due to thin air, which affects the heat dissipation of the UPS. The performance of electronic components inside the UPS will also be affected, which causes the sealed capacitor to bulge and further deteriorates the performance.

## Slide 10
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  UPS Configuration Solution
  UPS Capacity Calculation
  UPS Equipment Selection
  Battery Configuration

## Slide 11: Planning Method Overview
Determine the UPS networking solution.
Determine the capacity and number of a single UPS.
Determine the UPS type
(tower-mounted or modular UPS).
Determine the number and capacity of batteries in a battery string.
Determine the number of battery strings.
Battery configuration
UPS equipment
selection
Single UPS capacity
calculation
UPS configuration
solution

## Slide 12
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  UPS Configuration Solutions
  UPS Capacity Calculation
  UPS Equipment Selection
  Battery Configuration

## Slide 13: Typical UPS Configuration Solution (1)
Single UPS solution:
  The single UPS power supply solution is the simplest solution. In the solution, the output of a single UPS is directly connected to the load. This solution has no redundancy configurations and features low reliability. Single point of failure (SPOF) exists. Power supply should be disconnected when any component is faulty or needs overhauling.
  This solution is applicable to small power supply devices that require low reliability. The load power is about thousands of watts and this solution can be used only in Uptime Tier I data centers.
UPS
PDU
Load
Single UPS solution

## Slide 14: Typical UPS Configuration Solution (2)
Parallel UPS solution:
  This solution is more reliable than the single UPS power supply solution, but SPOF still exists.
  In this solution, there are two redundancy options for the UPS system: N+1 (N working UPS and one redundant UPS) and N+M (N working UPS and M redundant UPS). To reduce the cost, the N+1 parallel solution is recommended. To improve reliability, the N+M parallel solution is recommended.
  This solution is applicable to small and medium data centers. If the reliability level of the data center is Uptime Tier II, the UPS power distribution solution should at least use this redundancy solution.
UPS
PDU
Load
UPS
Parallel UPS (N+X) solution

## Slide 15: Typical UPS Configuration Solution (3)
Distributed redundancy solution
  In the distributed redundancy solution, three UPS groups are used. In normal cases, loads are evenly carried by the three UPS groups.
  If one UPS group is faulty, the loads will be carried by the other two UPS groups.
  In this scenario, loads are divided into several blocks, and each block uses dual power supplies.
  This solution is mainly used in large data centers and meets Uptime Tier Ⅲ requirements.
UPS1
PDU
Load1
UPS2
PDU
UPS3
PDU
Load3
Load2
Distributed redundancy solution
Notes: Advantages
  The solution facilitates online maintenance of all components (if all loads are dual-power loads).
  Compared with the 2N design, the solution has fewer UPS modules. Thus, its cost is lower. For any specific dual-power load, two independent power supplies are redundant .
  You do not need to transfer the loads to bypass mode for maintaining UPS modules, switch devices, and other power distribution devices. Maintenance bypass circuits usually do not need to be added in most distributed redundancy solution.
Disadvantages
  The cost is high as a large number of switch devices are used.
  The configuration solution is complex. In a large data center with multiple UPS, static transfer switches (STS), and power distribution units (PDU), it is a great task to keep each UPS system evenly loaded and to learn well about which system supplies power to which load.
  Unpredictable UPS running mode: Because UPS systems have various running modes and the systems can switch between multiple modes. It is impractical to test all these modes in a test environment with preset conditions and simulated faults to check whether the control policy and restored devices are functioning properly.
  The UPS efficiency is low because it does not work with full load.

## Slide 16: Typical UPS Configuration Solution (4)
Backup redundancy solution
  Four UPS groups form a power supply system. UPS group 4 and the first three UPS groups form a dual power supply system.
  Generally, UPS group 4 does not bear any load. However, when one UPS group in the primary circuit is faulty, UPS group 4 provides the backup power supply. Therefore, this solution has only one power supply. Although this solution meets the Uptime Tier III requirements, its reliability is lower than that of the distributed redundancy solution, the corresponding cost is also lower, which is applicable to some cloud-based data centers.
UPS1
PDU
Load
UPS2
PDU
UPS3
PDU
Load
Load
UPS4
PDU
Backup redundancy solution
Notes: The capacity of group 4 is variable. It can provide backup power for one load, multiple loads, or even all loads. However, power backup for all the loads cannot save device investment and goes against an original intention of this solution: saving costs.

## Slide 17: Typical UPS Configuration Solution (5)
Dual-bus solution 2N or 2(N+1)
  When the system is working properly, both power supply loops supply power to loads at the same time. Each loop carries half of the loads.
  In the case of a fault, if one loop is completely or partially faulty, the other loop can carry all the loads ensure that all loads run properly without power interruption.
  This solution is applicable to medium and large data centers. If the data center reliability level is Uptime Tier III or Tier IV, this solution is recommended for UPS power supply.
UPS
PDU
Load
UPS
PDU
Dual-bus system power supply solution
Notes: The advantages of this power supply solution are simple system, easy maintenance, high reliability, and no SPOF.
In actual design, the two UPS are physically isolated. They are placed in different power rooms. If a fire occurs in one room, the power supply of the UPS in the other room is not affected, ensuring uninterruptible power supply to loads.

## Slide 18: Solution Comparison (1)
Discussion: Assume that the load is 300 kW and the capacity of a single UPS is 75 kW. Compare the UPS capacity configurations and load rates of the five solutions. (The UPS can be fully loaded.)
Note:
  Three: The load is divided into three parts.
  Four: The load is divided into four parts.
 | Single UPS | N+1 Parallel UPS | DR Redundancy (three) | Backup Redundancy (four) | Dual-Bus
Load capacity | 300 kW | 300 kW | 300 kW | 300 kW | 300 kW
Single UPS | 75 kW | 75 kW | 75 kW | 75 kW | 75 kW
Number of UPSs |  |  |  |  | 
Total UPS capacity |  |  |  |  | 
UPS load rate |  |  |  |  | 
Solution comparison

## Slide 19: Solution Comparison (2)
According to the preceding analysis, the costs and reliability of these solutions are in direct proportion:
  Single UPS < N+1 parallel UPS < Backup redundancy < Distributed redundancy < Dual-bus
 | Single UPS | N+1 Parallel UPS | Distributed redundancy (three) | Backup Redundancy (four) | Dual-Bus
Load capacity | 300 kW | 300 kW | 300 kW | 300 kW | 300 kW
Single UPS | 75 kW | 75 kW | 75 kW | 75 kW | 75 kW
Number of UPSs | 4 | 5 | 3 x (1 + 1) | 4 + 1 | 4 + 4
Total UPS capacity | 300 kW | 375 kW | 450 kW | 375 kW | 600 kW
UPS load rate | 100% | 80% | 66.7% | 80% | 50%
Networking solution comparison
Notes: Note: This table briefly displays the total capacity and actual UPS efficiency of each solution. Only qualitative analysis is performed. The actual cost and efficiency involve specific loads and UPS capacity.
The backup redundancy solution is the same as the N+1 parallel UPS solution in terms of the UPS. However, the backup redundancy solution requires a large number of switch cabinets and cables, which is more expensive and more reliable than the N+1 parallel UPS solution.

## Slide 20: Solution Comparison (3)
Configuration | Used in the Past | Reason for Use
No redundancy | Small companies Companies with multiple local offices Companies with geographically redundant data centers | Reduced investment and energy costs Support for less critical applications Simple configuration and installation Power-off maintenance is allowed
Parallel redundancy | Small and medium companies with data centers whose IT capacity is usually less than 500 kW | Better fault tolerance than "N" Loads can be added in the future
Distributed redundancy | Large companies with data centers whose IT capacity is usually greater than 1 MW | Online maintenance is supported More economical than "2N"
Dual-bus | Large MW-level data center | Full redundancy between path A and path B Easier to balance loads of the UPS system
Application scenarios of different solutions
Notes: How to select the most suitable configuration solution? Let's review the precautions to be considered when selecting a proper configuration:
  Breakdown cost/impact: How much cash flow does the company have per minute? If a fault occurs, how long does it take for the system to recover? The answers to the above questions can be used as the beginning of the budget solution discussion. The discussion direction varies with the answer.
  Budget: In any aspect, the cost of implementing the 2(N+1) design is much higher than that of the N (capacity) design, parallel redundancy design, or even distributed redundancy design. Let's take a large data center as an example to see the cost gap. If the data center uses the 2(N+1) design, thirty 800 kW modules may be required (each parallel bus has five modules, and there are six parallel buses in total). For the same load, if the distributed redundancy design is used, only eighteen 800 kW modules are required, and the cost is much lower.
  IT architecture type: Virtualization and rapid improvement of network bandwidth and speed enable the entire data center to be switched to another site without delay. This also raises questions about the perception that data centers with the highest availability are facilities with highly redundant power and cooling architectures. As the virtualization technology matures, two distant "N" system data centers may have higher availability than a highly redundant data center.

## Slide 21
Notes:   Availability: How long can the company tolerate downtime in a year? If the answer is never to shut down, then the high availability design should be chosen in the budget. However, if the company allows shutdown after 10 p.m. every night and at most weekends, then the parallel redundancy design is recommended for the UPS configuration. Some parts of each UPS need maintaining. And some unexpected faults will occur in the UPS from time to time. The less the time used in maintenance is, the more redundant components are required.
  Reliability: The higher the reliability of a UPS, the higher the probability of continuous operation of the system.
  Maintainability: Long-time system breakdown caused by faults cannot be prevented by high reliability.

## Slide 22
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  UPS Configuration Solution
  UPS Capacity Calculation
  UPS Equipment Selection
  Battery Configuration

## Slide 23: UPS Capacity Calculation (1)
The N+1 and 2N configurations are widely used in the industry. Therefore, it is crucial to calculate and obtain the N value of the UPS system.
N is the basic requirement, that is, the UPS system capacity in a non-redundancy solution. In actual applications, N has gradually become the number of UPS (or modules) that meet the basic load power requirements without redundancy.
Notes: 1.2 is a coefficient, and E ≥ 1.2 P. E is the basic capacity of the UPS, and P is the calculated load of the electronic information equipment.
Power factor description:
  Input power factor (cos φ1): indicates a UPS's rectification and correction capability of the UPS and loads.
  Output power factor (cos φ2): indicates the active power output capability of a UPS.
  Load power factor (cos φ3): varies with products. The power factor of IT equipment ranges from 0.98 to 1, that of Huawei air-cooled DX air conditioners is 0.9, that of Huawei water-cooled indoor units is 0.94, and that of pumps ranges from 0.8 to 0.9.

## Slide 24: UPS Capacity Calculation (2)
To calculate N, you must know the following values:
  Active power for actual loads (P), measured in W or kW.
  Expected power of a single UPS (Pn), measured in W or kW.
  Expected UPS output power factor (cos φ). For details about the power factor, see the figure on the right.
  N = Round up (P/cos φ x 1.2)/Pn
UPS power factor illustration
Transformer/Diesel generator
Load
Input power factor cos φ1
Load power factor cos φ3
Output power factor cos φ2
Notes: 1.2 is a coefficient, and E ≥ 1.2 P. E is the basic capacity of the UPS, and P is the calculated load of the electronic information equipment.
Power factor description:
  Input power factor (cos φ1): indicates a UPS's rectification and correction capability of the UPS and loads.
  Output power factor (cos φ2): indicates the active power output capability of a UPS.
  Load power factor (cos φ3): varies with products. The power factor of IT equipment ranges from 0.98 to 1, that of Huawei air-cooled DX air conditioners is 0.9, that of Huawei water-cooled indoor units is 0.94, and that of pumps ranges from 0.8 to 0.9.

## Slide 25: UPS Capacity Calculation (3)
Example: The actual active power of loads is 1000 kW. Huawei UPS5000-E series are used to meet the N+1 backup requirement. The UPS system configuration is provided as follows.
The calculation process is as follows:
  For the UPS500-E series, the output power factor is 1, the load power factor is 0.9, and the capacity of a single UPS is 125 kVA, 200 kVA, 300 kVA, 400 kVA, 500 kVA, 600 kVA, or 800 kVA. The N value of different capacities are calculated as follows:
  When the capacity of a single UPS is 300 kVA: N = (1000/0.9 x 1.2)/300 ≈ 5.
  When the capacity of a single UPS is 500 kVA: N = (1000/0.9 x 1.2)/500 ≈ 3.

## Slide 26: UPS Capacity Calculation (4)
The calculation process is as follows:
  Considering that four UPS can be configured at most in an N+1 parallel system, you can select four 500 kVA UPS to form an N+1 system.
  If the system is expanded to the 2N architecture, you can configure two groups with three 500 kVA UPS in each group. Thus, a total of six UPS are configured.
  In the 2(N+1) architecture, you can configure two groups with four 500 kVA UPSs in each group. Thus, a total of eight UPS are configured.

## Slide 27
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  UPS Configuration Solution
  UPS Capacity Calculation
  UPS Equipment Selection
  Battery Configuration

## Slide 28: Comparison Between Modular UPS and Traditional UPS (1)
Modular UPS VS
Traditional UPS
Capacity expansion:
The modular UPS is easy to expand.
Maintenance: The modular UPS is easy to maintain.
Redundancy: The modular UPS is easier to implement N+1 redundancy.
Efficiency: The modular
UPS has high efficiency.
Performance differences
Notes: The modular UPS is easy to expand. You only need to purchase the required power module (about 50 kVA) for future capacity expansion, which does not require cable reconstruction. Tower-mounted UPSs can be expanded by adding power units. However, the power unit is large (usually 100 kW or 200 kW), which cannot meet the requirement of flexible configuration due to the increase of the load. Thus, before expanding capacities for a tower-mounted UPS, you need to shut down the UPS.
The modular UPS has high efficiency and saves energy. The high efficiency of a modular UPS depends on the flexibility of power configuration. When the load is light, the power module hibernation technology ensures that the UPS works at the maximum efficiency. However, the efficiency of a tower-mounted UPS is greatly reduced due to the large power unit.
The modular UPS itself is a redundancy solution. When one module in the modular UPS is faulty, the module can be hot-swapped quickly and maintained with the power on. To maintain some of the parts in the tower-mounted UPS, the UPS has to transfer to bypass mode, which decreases the reliability of the UPS.
It is easier to implement N+1 redundancy in modular UPSs. For example, in a 400 kVA system, the original 1+1 configuration requires 800 kVA, and one module can be used for redundancy. The 450 kVA configuration with 50 kVA modules implements (8+1) redundancy.

## Slide 29: Comparison Between Modular UPS and Traditional UPS (2)
Cost comparison
TCO
OPEX
Maintenance
cost
Deployment
cost
CAPEX
Equipment
cost
Operation cost
Equipment hardware cost
Equipment software cost
Auxiliary equipment cost
Equipment installation cost
Civil work cost
Equipment transportation cost
Site renting
Equipment power consumption
Maintenance cost
Service cost
Labor cost
Notes: TCO: Total cost of ownership
CAPEX: Capital expenditure
OPEX: Operating expense

## Slide 30: Comparison Between Modular UPS and Traditional UPS (3)
Equipment cost: The cost of a modular UPS is about 30% higher than that of a traditional tower-mounted UPS.
Deployment cost: Traditional tower-mounted UPS are integral, and modular UPS are small. Therefore, the deployment cost of modular UPS is small.
Operation cost: The modular UPS is easy to expand. As modules are gradually deployed along with the project progress, the efficiency is high. Therefore, a large amount of electricity fees can be saved.
Maintenance cost:
  Tower-mounted UPS are difficult to maintain. Once a fault occurs, only professional personnel from the manufacturer can maintain the UPS. Thus, the maintenance cost is high.
  The modular UPS adopts the modular design. If a module is faulty, it can be directly replaced. The faulty module can be sent to the manufacturer for repair, which greatly reduces the labor cost and the round-trip cost of professional personnel from the manufacturer.

## Slide 31: Comparison Between Modular UPS and Traditional UPS (4)
Summary
  The traditional UPS features low CAPEX, while the modular UPS features low OPEX. These advantages can be converted based on different scenarios. If the customer requires N+1 redundancy, the modular UPS can greatly reduce the CAPEX.
  In the first three years, the TCO of tower-mounted UPS is low. In the fourth year, modular UPS have obvious cost advantage. Take the mainstream data center UPS with the lifetime of 8 to 10 years as an example. The advantages of modular UPSs are obvious.

## Slide 32
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  UPS Configuration Solution
  UPS Capacity Calculation
  UPS Equipment Selection
  Battery Configuration

## Slide 33: Single UPS Configuration (1)
There are two methods for configuring the battery capacity: constant current method and constant power method. The constant power method is widely used in the industry because it is more accurate. Here, the constant power method is introduced.
Parameters required for configuring the battery capacity of a single UPS
  Active power for loads (P), measured in W or kW
  Battery inversion efficiency (η)
  Number of 12 V batteries (n)
  Expected battery constant power discharge table
Notes: Single UPS configuration refers to the configuration of a single UPS instead of an N system, because an N system can also be a parallel system.

## Slide 34: Single UPS Configuration (2)
The calculation is performed using the following method:
  Calculate the required discharge power of each battery cell: W = P/η/(n x 6).
  Compare the battery constant power discharge table to obtain the configuration of four or fewer battery strings with the power deviation ranging from –5% to +10%.
  Use the UPS charging current to check whether the UPS meets the charging requirements.
  Select the most economical solution.

## Slide 35: Single UPS System Configuration Example (1)
Example: A single UPS5000-E-80K is configured, η is 0.97, the actual load is 32 kW, a single battery string contains 32 batteries (12 V), and the backup time is 15 minutes.
Calculation process:
  W = 32000/0.97/32/6 = 172W/cell
  Look up the table for 1.67 V–15 min.
  Select two 26 Ah battery strings.
26 Ah constant power discharge table of a brand

## Slide 36: Single UPS System Configuration Example (2)
Calculation process
  Check whether the UPS charging power meets requirements:
    Calculate the UPS battery charging power as follows: when the charging power is: N_group x N_bat x 2.35 x 0.1 x C_ah (W), the charge power is: 2 x 32 x 6 x 2.35 x 0.1 x 26 = 2346.24 W.
      N_group: number of battery strings for a single UPS
      N_bat: number of cells in a battery string. A 12 V battery contains six cells.
      C_ah: capacity of a single battery, measured in Ah
      2.35 V: equalized charging voltage of a single battery
      2.35 x 0.1 x C_ah: charge power of each cell
Notes: Pay special attention to check whether the UPS charge power meets the requirements for long backup time of a small-capacity UPS as excessive batteries will affect the battery lifespan.
If the battery charge current does not meet the requirement, the charge time is prolonged. If the power is unstable, the batteries cannot be fully charged for a long time, which causes great damage to the batteries.

## Slide 37: Single UPS System Configuration Example (3)
Calculation process
  Check whether the UPS charging power meets requirements:
    The charge power of a single UPS5000-E module is 10% of the module capacity. The charge power of the UPS5000-E-80K is 8 kW (the capacity of each power module is 40 kVA). Therefore, the charge power meets the requirements.
Notes: Pay special attention to check whether the UPS charge power meets the requirements for long backup time of a small-capacity UPS as excessive batteries will affect the battery lifespan.
If the battery charge current does not meet the requirement, the charge time is prolonged. If the power is unstable, the batteries cannot be fully charged for a long time, which causes great damage to the batteries.

## Slide 38: Single UPS System Configuration Analysis (1)
Load power, power factor, and inverter efficiency
End-of-discharge (EOD) voltage and discharge time
Number of batteries
Battery capacity

## Slide 39: Single UPS System Configuration Analysis (2)
Load power, power factor, and inverter efficiency
  The rated output power of the UPS is expressed in the form of apparent power kVA. The actual maximum output power of the UPS is the kVA multiplied by the UPS output power factor. From the perspective of load usage, the output power factor of the UPS is the input power factor of the load, which varies with the load power. For example, if the nominal power of a load is 1000 VA and the input power factor is 0.7, the actual maximum power is 700 W. Currently, some AC devices use the power factor correction (PFC) circuit to ensure that the power factor is greater than 0.9. The power factor for common loads is 0.9.
  The UPS efficiency refers to the system efficiency, that is, the overall conversion efficiency of the current after rectification and inversion when the UPS works properly. The battery inversion efficiency refers to the conversion efficiency of the current passing through the battery, inverter circuit, and load when the battery is discharging. Generally, the efficiency is higher than the UPS system efficiency. The battery inversion efficiency of Huawei UPS5000 series is usually calculated based on 95%.

## Slide 40: Single UPS System Configuration Analysis (3)
EOD voltage and discharge time
  Why is the battery EOD voltage 1.67 V/cell in the example?
    Generally, if the battery backup time is less than 1 hour, the EOD voltage is 1.67 V/cell. If the battery backup time is 1 to 3 hours, the EOD voltage is 1.75 V/cell. If the battery backup time is greater than 3 hours, the EOD voltage is 1.80 V/cell.
Notes: Take a 150 Ah battery as an example. The discharge current is fixed at 15 A. After the battery is discharged for 10 hours, the discharge capacity is 150 Ah. In this case, the battery voltage should be about 1.8 V. If the battery continues discharging, the battery may be damaged.
Theoretically, if the discharge current is different and the total discharge capacity equals the rated battery capacity, the EOD voltage should be about 1.8 V. Actually, the larger the battery discharge current (the shorter the discharge time), the lower the discharge capacity. Take SD150 as an example. When the discharge time is 4 hours, the discharge voltage is 1.8 V, and the EOD voltage is 1.8 V, the power of a single cell is 63.3 W, and the total energy discharged within 4 hours is 253.2 Wh (4 x 63.3 = 253.2 Wh). When the discharge time is 1 hour, and the EOD voltage is 1.8 V, the power of a single battery is 173 W, and the total energy discharged within 1 hour is 173 Wh (1 x 173 = 173 Wh).

## Slide 41: Single UPS System Configuration Analysis (4)
EOD voltage and discharge time
  Why does the EOD voltage vary with the discharge time?
    The battery capacity is expressed in Ah, that is, the current multiplied by time. Battery manufacturers usually use a constant current to discharge batteries for 10 or 20 hours, that is, the discharge rate of C10 or C20. That is, a normally fully charged battery discharges for 10 hours or 20 hours at the rated current, and the discharged capacity is just equal to the nominal capacity of the battery. In this case, the terminal voltage of the battery is 1.8 V (2 V cell).
    When the EOD voltage is the same, the larger the discharge current (shorter time), the smaller the total discharge capacity. Therefore, when the discharge time is short, the EOD voltage needs to be reduced to ensure sufficient discharge capacity. (After the battery discharge reaches the EOD voltage, it is difficult to discharge more capacity and the battery may be damaged.)
Notes: Take a 150 Ah battery as an example. The discharge current is fixed at 15 A. After the battery is discharged for 10 hours, the discharge capacity is 150 Ah. In this case, the battery voltage should be about 1.8 V. If the battery continues discharging, the battery may be damaged.
Theoretically, if the discharge current is different and the total discharge capacity equals the rated battery capacity, the EOD voltage should be about 1.8 V. Actually, the larger the battery discharge current (the shorter the discharge time), the lower the discharge capacity. Take SD150 as an example. When the discharge time is 4 hours, the discharge voltage is 1.8 V, and the EOD voltage is 1.8 V, the power of a single cell is 63.3 W, and the total energy discharged within 4 hours is 253.2 Wh (4 x 63.3 = 253.2 Wh). When the discharge time is 1 hour, and the EOD voltage is 1.8 V, the power of a single battery is 173 W, and the total energy discharged within 1 hour is 173 Wh (1 x 173 = 173 Wh).

## Slide 42: Single UPS System Configuration Analysis (5)
Number of batteries
  According to the calculation formula, the battery configuration varies with the number of batteries. In some special cases, batteries are over-configured to ensure that the battery capacity meets the customer‘s requirements (if the number of batteries supported by the UPS is variable). In this case, if you configure an appropriate number of batteries, the overall cost can be reduced on the premise that the customer’s requirements are met.

## Slide 43: Parallel System Configuration (1)
The battery calculation in a parallel UPS system is the same as that in a single UPS system. However, considering factors such as costs and space, the battery calculation in a parallel UPS system can be optimized. The solutions in descending order of cost are as follows: single UPS power backup (highest reliability) > system power backup > battery string sharing (lowest reliability).
Single UPS power backup solution
  Each UPS is equipped with one or more battery strings. When a UPS is faulty, the UPS and the battery strings connected to it exit the parallel system, and the remaining battery strings can supply sufficient power to the UPS.
  Example: The load is 300 kVA, three 200 kVA UPSs are used to form a 2+1 system, and the backup time is 10 minutes.
Notes: The parallel system refers to the N+X solution. The N+1 solution is used as an example. The dual-bus system will be described later.

## Slide 44: Parallel System Configuration (2)
Single UPS power backup solution
  When single UPS power backup is used, batteries can be configured based on the single UPS load power of 150 kVA (300/2=150 kVA) for 10 minutes. Each UPS is configured with the same battery string.
  Note: In this solution, the backup time is longer than the time required by the customer when the UPS system works properly. When the redundant UPS is faulty and exits the system, the backup time of the entire UPS system can still meet the requirements.
Notes: The parallel system refers to the N+X solution. The N+1 solution is used as an example. The dual-bus system will be described later.

## Slide 45: Parallel System Configuration (3)
System power backup solution
  If the customer does not specify the backup time of a single UPS, batteries can be configured in load balancing mode. In this case, when all UPSs are working, the system backup time can be ensured. However, if one UPS is faulty (the battery string is unavailable), the remaining battery strings cannot reach the required backup time.
  Example: If the load is 300 kVA, 200 kVA UPSs are connected to form a 2+1 system, and the backup time is 10 minutes, batteries can be configured based on the single UPS load power of 100 kVA (300/3 = 100 kVA) for power backup of 10 minutes.

## Slide 46: Parallel System Configuration (4)
System power backup solution
  If the load power is 500 kVA, 200 kVA UPSs are connected to form a 3+1 system, and the backup time is 10 minutes, batteries can be configured based on the single UPS load power of 125 kVA (500/4 = 125 kVA) for power backup of 10 minutes.
  Note: The backup time of the entire system meets the requirements only when the UPSs work properly. If the redundant UPS is faulty and exits the system, the backup time cannot meet the requirements.

## Slide 47: Parallel System Configuration (5)
Battery string sharing solution
  To reduce the overall cost, the battery string sharing solution can be used. When battery strings are shared, all battery strings and UPSs are connected to the same busbar.
  Advantages: Because battery strings are directly connected in parallel, they can be configured for one UPS. Battery strings do not need to be evenly distributed to each UPS. In some scenarios, costs can be reduced. (If the total capacity is the same, the cost of a small number of battery strings is low. For example, three 400 Ah battery strings are cheaper than four 300 Ah battery strings. In addition, related accessories such as battery racks and switch boxes are fewer.)
  Disadvantage: SPOF may occur. If one battery string is faulty, all batteries may be unavailable. In actual applications, each battery string should be configured with an independent switch.

## Slide 48: Parallel System Configuration (6)
Comprehensive comparison of configuration solutions:
  A 2+1 parallel system consisting of 200 kVA UPSs for 300 kVA loads is used as an example. The backup time is 15 minutes.
  Note: The price in the table includes the prices of the battery rack and battery switch and is the price of the entire battery system.
Battery backup solution | Battery | Price (¥) | Reliability
Single UPS power backup | 3 x (100 Ah, three strings, 32 batteries) | 475,137 | High
System power backup | 3 x (100 Ah, two strings, 32 batteries) | 308,628 | Relatively high
Battery string sharing | 150 Ah, four strings, 32 batteries | 293,329 | Medium
Battery string sharing + Battery quantity adjustment and optimization | 100 Ah, four strings, 40 batteries | 244,985 | Medium
Solution cost comparison
Notes: Conclusion:
  Battery configurations cannot be accurately matched. To meet customer requirements, over-configuration often occurs.
  Compared with single UPS power backup, system power backup reduces the cost by about 35%.
  Compared with single UPS power backup, battery string sharing reduces the cost by about 40%.
  By adjusting the number of batteries, the cost can be reduced by about 12% compared with the solution with a fixed number of batteries.
The total cost is the lowest when battery strings are shared and the number of batteries is adjusted. Compared with the maximum configuration solution, the cost is reduced by about 50%. In a common UPS configuration solution, the battery string cost accounts for 20% to 40% of the total cost. If the backup time is long, the battery string cost may even exceed the UPS price. Therefore, it can be concluded that the UPS solution quotation can be reduced by 10% to 30% by optimizing the battery string configuration.

## Slide 49: Parallel System Configuration (7)
Dual-bus system
  System power backup solution
    The loads of the dual-bus system are balanced. Path A carries half of loads while path B carries the other half. The battery configuration can be reduced, and the entire system can still meet the customer's requirements. However, this solution reduces the system availability.
  Single UPS power backup solution
    Both path A and path B can meet the basic capacity and designed backup time. Path A can fully back up path B. For the UPS system, this solution is a dual-bus system in the strict sense.

## Slide 50
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  UPS Configuration Solution
  UPS Capacity Calculation
  UPS Equipment Selection
  Battery Configuration

## Slide 51
(short-answer question) What are the advantages and disadvantages of a distributed redundant system compared with a dual-bus system?
(short-answer question) What are the battery configuration solutions for a parallel UPS system?
Notes: 1. Answer
  Advantage: The UPS load rate of the system is higher than that of 2N when two power supplies are available, which reduces costs.
  Disadvantage: The system operation and maintenance (O&M) are complex because loads need to be partitioned. When a load is added, the group to which the load is added must be specified. The loads of all UPS groups must be basically the same.
2. Answer
  Single UPS power backup solution: The number (N) of requisite UPSs is used for calculation. The actual backup time exceeds the required time. If the redundant UPS is faulty, the backup time of the system can still meet the requirements.
  System power backup solution: The number of all UPSs is used for calculation. The backup time meets requirements only when all UPSs in the system are running properly. If one UPS is faulty, the remaining UPSs cannot meet the backup time requirements.
  Battery string sharing solution: All battery strings are connected to the UPS through a bus. The cost is low, but the reliability is reduced accordingly.

## Slide 53
V5R2
V1R1
2019.01.25
Update
Chen Kaifeng/cwx377854
2020.4.11
Li Shaofeng/ l0486775
New
2019.01.25
Update
2019.01.25
Update
2019.01.25
Update
2019.01.25
Update