## Slide 1: Data Center Low-Voltage Power Distribution System Planning

## Slide 2
System Composition
Planning Preparation
Planning Method

## Slide 3: System Scope
The following figure shows the position of a low-voltage power distribution subsystem in a power supply and distribution system.

## Slide 4: System Overview
Main components
  A low-voltage power distribution system consists of a low-voltage power distribution frame (PDF) and power cables.
  The low-voltage PDF leads in the low-voltage mains output from the transformer, distributes the mains to the uninterruptible power system (UPS) PDF, DC PDF, and power PDF, which distribute the mains power to loads.
  Power cables are used to connect systems at all levels and lead power from the mains to loads. Conductors include cables and busways, and they have different application scenarios.
Step-down transformer
Low-voltage PDF
Diesel generator (DG)
DC PDF
UPS PDF
Air conditioner PDF
Components of a low-voltage power distribution system
Notes: The low-voltage power distribution system of a data center refers to the power distribution system with an AC voltage of 1200 V or lower.
The low-voltage PDF consists of the circuit breaker, fuse, load switch, automatic transfer switch (ATS), and electric energy metering device.

## Slide 5
System Composition
Planning Preparation
Planning Method

## Slide 6: Planning Preparation - Requirement Input
Data center levels determine the power supply solution for loads, for example, single or dual power supplies.
Load power and voltage modes determine the capacity and type of low-voltage electric devices, for example, single-phase circuit breakers or three-phase circuit breakers.
Notes: The data center reliability level should be determined. Generally, for Tier III or higher, the dual power supply solution is used to provide two independent power supplies for dual-power loads such as ICT equipment, air conditioners, fire extinguishing devices, and lighting devices. For Tier IV, each subsystem adopts the 2N redundancy mode. If Tier II or lower is required, the single power supply solution is generally used for loads. The implementation of these two solutions must comply with relevant standards such as Uptime or TIA-942.
In the dual power supply solution, to ensure that the entire IT loads run normally when one power supply fails, the low-voltage electric device and conductor specifications of each power supply should be determined to support the load rate of 100%.
If the dual power supply solution is used for single-power loads in the data center, such as air conditioners, lighting devices, and even ICT equipment, the ATS, manual transfer switch (MTS), or static transfer switch (STS) (for single-power service loads) is required. When one power supply is faulty, the ATS/MTS/STS switches to the other power supply to ensure power supply. For dual-power loads, use dual power supplies.

## Slide 7
System Composition
Planning Preparation
Planning Method
  Planning Procedure
  Power Supply Solution Selection
  Low-voltage Electric Device Selection
  PDF Configuration
  Conductor Selection

## Slide 8: Planning Procedure
Collect statistics on the load levels of IT devices, lighting, fire extinguishing devices, and chillers. Select a power supply solution based on the load level: single power supply or dual power supplies.
Determine the specifications and number of main low-voltage electric devices, such as circuit breakers and ATSs.
Based on the low-voltage electric device selection, determine the number of PDFs, PDF specifications, and the number of incoming cables.
Determine the conductor type (cable or bus).
PDF configuration
Low-voltage electric
device selection
Load level and power
supply solution selection
Conductor selection

## Slide 9
System Composition
Planning Preparation
Planning Method
  Planning Procedure
  Power Supply Solution Selection
  Low-voltage Electric Device Selection
  PDF Configuration
  Conductor Selection

## Slide 10: Typical Power Supply Solution (1)
Notes: The single power supply solution on the left is often used in the Tier I or Tier II data centers. If you want to improve reliability or dual power supply IT loads are used, you can use the pseudo dual power supply solution on the right.

## Slide 11: Typical Power Supply Solution (2)
Notes: Note that the preceding figure is a rough topology. The final design prevails.
The dual power supply solution is generally used in Tier III or higher data centers. For key loads such as air conditioners, lighting, and fire extinguishing devices, an ATS needs to be configured to facilitate online maintenance.
In the dual power supply solution, a bus tie switch can be configured to improve reliability.

## Slide 12
System Composition
Planning Preparation
Planning Method
  Planning Procedure
  Power Supply Solution Selection
  Low-voltage Electric Device Selection
  Low-Voltage PDF Configuration
  Conductor Selection

## Slide 13: Calculating the Capacity of Low-Voltage Electric Devices
Current calculation method
  Measure the active power of each load, and calculate the current using the following formulas. The rated current of a low-voltage electric device is equal to the calculated current multiplied by a coefficient ranging from 1.2 to 2.0.
  Single-phase load: ,
    where: : single-phase voltage; : power factor; : active power; : calculated current;
  Three-phase load:
    where: : line voltage; : power factor; : active power; : calculated current.

## Slide 14: Low-Voltage Electric Device Selection - Circuit Breaker
Circuit breaker classification:
  The miniature circuit breaker (MCB) is installed at the upstream side of small loads or on the PDU in the cabinet. Its operating current is less than 100 A.
  The molded case circuit breaker (MCCB) applies to medium-sized loads, such as medium-sized UPS PDFs. Its operating current ranges from 100 A to 1000 A.
  The air circuit breaker (ACB) is mainly used in the low-voltage main PDF. Its operating current is generally greater than 1000 A.
In the low-voltage power supply system of a data center, the initial rated current of low-voltage electric devices such as circuit breakers is determined based on the calculated operating current.
For example, if the total capacity of the single-phase load is 20 kW, the calculated current I = 20000/(220 x 0.8) = 113.6 A. Multiply the calculated current by the coefficient 1.23. The rated current of the circuit breaker to be selected In is 140 A. If the heat dissipation condition of the PDF is poor, select a 160 A circuit breaker.
Hierarchical protection should be used in the power distribution system of data centers.
Notes: In the low-voltage power supply system of a data center, the initial rated current of low-voltage electric devices such as circuit breakers is determined based on the calculated current.
According to the related standard, the rated current of a circuit breaker is tested on a separate circuit breaker without shells. Therefore, if the device is installed in a power distribution box (PDB) or PDF with poor heat dissipation, the circuit breaker capacity should be derated to 0.7–0.8. For other low-voltage electric devices such as fuses, the rated current calculation is similar to that of circuit breakers, that is, by multiplying the calculated current by the corresponding coefficient.
In the power distribution system of a data center, hierarchical protection should be used. That is, if a system has multiple levels of circuit breakers, the rule of selecting circuit breakers is to ensure that when a circuit breaker at a certain level is faulty, only the circuit breaker at the corresponding level trips and the power of other levels is not affected. Therefore, a circuit breaker should have a lower capacity than the upstream one and larger capacity than the downstream one.

## Slide 15: Low-Voltage Electric Device Selection - ATS
The ATS is used to automatically switch between the mains supply and the DG supply, or to provide dual power supplies for devices such as air conditioners. The STS is used to provide dual power supplies for single-power critical loads. The selection rules are as follows:
  The ATS and STS should be selected based on the rated operating voltage and calculated current. The rated current of the selected device should be greater than or equal to the calculated current.

## Slide 16: ATS Typical Application Solution (1)
Working logic:
  When a mains outage occurs, the ATS sends a startup signal to start the standby generator.
  The ATS automatically detects the voltage and frequency of the standby generator. When the voltage and frequency reach the rated values, the ATS automatically switches to the generator supply.
  After the mains is restored and stable, the ATS automatically switches back to the mains supply.
  The ATS sends a stop signal to shut down the standby generator after DG cold start.
This solution applies to scenarios that require low costs and low reliability.
ATS
Mains
Emergency generator
Load A
Non-critical load
Switchover between one mains input
and one standby generator
Notes: Note: The figure only displaies the switching between the DG and mains. The power supply topology of loads is not displayed.

## Slide 17: ATS Typical Application Solution (2)
If the customer wants to improve the power supply reliability, how to configure a standby DG or mains?
  1 mains supply + 2 DGs (one active and one standby)
  2 mains supplies (one active and one standby) + 1 DG

## Slide 18: ATS Typical Application Solution (3)
Switchover between one mains input and two standby generators
  If the mains supply fails, the generator G1 starts and ATS 1 switches to the generator.
  If both the mains supply and G1 generator supply fail, the G2 generator starts and ATS 2 switches to the G2 generator.
  In this solution, when the mains supply fails, the generator directly carries the load. There is a redundant generator, so the reliability is relatively high.
  This solution applies to scenarios where the mains supply is normal and high reliability is required.
G1
generator
ATS1
ATS2
Mains
Load
G2 standby
generator
Switchover between one mains input and two standby generators

## Slide 19: ATS Typical Application Solution (4)
Switchover between two mains inputs and one standby generator
  If mains 1 or 2 fails, the generator is not started, and ATS1 switches to mains 1 or 2.
  When both mains 1 and mains 2 fail, the generator starts, and ATS2 switches to the generator.
  This solution has high reliability when the mains supply is normal. If the mains supply is unavailable, the DG directly carries the load, and the reliability is relatively low.
  This solution applies to scenarios where the mains supply is good and high reliability is required.
Mains 1
Load
Mains 2
Emergency generator
ATS 1
ATS 2
Switchover between two mains inputs and one standby generator

## Slide 20: ATS Typical Application Solution (5)
If the customer requires higher power supply reliability and wants to deploy two mains inputs and multiple standby generators, how to achieve this?
Mains 1
Mains 2
Emergency generator
Bus tie switch
Load
Load
Switchover between two mains inputs and multiple standby generators

## Slide 21: Reactive Power Compensation
In a data center, reactive power compensation is required for low-voltage power supply to achieve the required power factor and improve the power grid quality. The formula for calculating reactive power compensation is as follows:
  is the angle of the power factor before the compensation.
  is the angle of the power factor after the compensation.
  P is the active power.
Then select the corresponding capacitor based on the calculated reactive power.
Notes: Obtain the active power, reactive power, and apparent power of all devices. Calculate the power factor of the current data center based on the active power, reactive power, and apparent power, and calculate the reactive power to be compensated based on the formula.
The power factor after compensation should be 0.9 or above.

## Slide 22: Example of Reactive Power Compensation
Load statistics of a data center:
  Active power: 2739.47 kW; reactive power: 1701.81 kVar; total apparent power: 3225 kVA; current power factor: 0.85; power factor after compensation: 0.9.
The calculation is as follows:
= 2739 x (0.619 – 0.4843) = 369 kVar
  After compensation: active power: 2739.47 kW, reactive power: 1332.81 kVar, total apparent power: 3043 kVA, power factor: 0.9.

## Slide 23
Determine which loads are powered by the UPS and which loads are powered by the mains.
Complete the preliminary power supply solution. For loads with dual power supplies, use dual power supplies. For important loads with a single power supply, use dual power supplies and ATS/STS switching.
Understand the switchover solution between the mains supply and DG.
Estimate the reactive power compensation scale.
Calculate the capacity of low-voltage electric devices for different loads and the number of low-voltage electric devices, for example, the low-voltage electric devices numbers for UPSs, chillers, and other power equipment such as the cooling water pump. This helps determine the number and capacity of low-voltage PDF.

## Slide 24
System Composition
Planning Preparation
Planning Method
  Planning Procedure
  Power Supply Solution Selection
  Low-voltage Electric Device Selection
  Low-Voltage PDF Configuration
  Conductor Selection

## Slide 25: Low-Voltage PDF (1)
The main low-voltage PDF is the load control center in a data center. It is a set of combined cabinets including the cable entry cabinet, reactive power compensation cabinet, bus-tie cabinet, and feeder cabinet.
Passing through a transformer, the high-voltage mains supply is stepped down and connected to the general switch of the cable entry cabinet. The output end of the general switch is connected to the bus of the PDF. The current passes the feeder cabinet, reactive power compensation cabinet, and bus-tie cabinet through the bus. The bus-tie cabinet is used to switch between multiple power supplies.
  Note: If two power inputs are required for important loads, use a bus-tie cabinet to connect the two main low-voltage PDFs to improve system reliability. In normal cases, the two low-voltage PDFs run separately, and the bus interconnection switch is turned off. When one mains supply is faulty, the bus interconnection switch is turned on, and the normal mains supplies power to loads.

## Slide 26: Low-Voltage PDF (2)
Based on the calculated number and size of low-voltage electric devices such as circuit breakers and the power supply system diagram, determine the number and capacity of PDFs, and determine the position of each PDF and the number of loads connected to each PDF.
Common PDFs used in data centers are GGD, GCK, GCS, and MNS (in China). The GGD is a fixed PDF, and the other three are drawable PDFs.
GGD
GCS
GCK
MNS
Notes: The GGD AC low-voltage PDF applies to the power distribution system with the AC frequency of 50 Hz, rated operating voltage of 380 V, and rated operating current of less than 3150 A. It is used to convert, distribute, and control power for power, lighting, and power distribution devices. The disadvantages of the GGD are that the loop is few, the units cannot be combined arbitrarily, the footprint is large, and it cannot communicate with the computer.
The GCK low-voltage drawable switch cabinet consists of a power distribution center (PC) and a motor control center (MCC). It is applicable to the power distribution system with an AC frequency of 50 Hz, a rated operating voltage of less than or equal to 660 V, and a rated current of 6300 A or lower. It can distribute power for power devices and lighting and control motors. The cabinet is made of type-C materials, and the height of a standard unit (E) is 25 mm.
The GCS low-voltage drawable switch cabinet is used in a power supply/generation system with a three-phase AC frequency of 50 Hz, rated working voltage of 400 V (690 V) and rated current of 4000 A or lower. It controls the power devices and motors, distributes power, and compensates capacitance. The cabinet can be operated only from one side. The cabinet is made of type-KS materials, and the height of a standard unit (E) is 20 mm.
The MNS cabinet can be operated from two sides. The depth of the cabinet is 600 mm, 800 mm, or 1000 mm, and the supported current of the cabinet reaches 6300 A. The cabinet is made of type-C materials, and the height of a standard unit (E) is 25 mm.

## Slide 27
Notes: Drawable cabinet:
  The height of the cabinet is 2200 mm, and the effective height of drawers (that is, the height of drawers) is 1800 mm. Therefore, the two types of cabinets can be installed with nine layers of drawers. 8E (E = 20/25) = 160/200: The drawer heights are less than 1800.
  In the following example, E=25.
  8E/4 = 200/4 (indicating that four drawers are placed in the space of 200 mm high and the width is 150 mm)
  8E/2 = 200/2 (indicating that two drawers are placed in the space of 200 mm high and the width is 300 mm)
  8E: The drawer height is 200 mm and the width is 600 mm. 12E: The drawer height is 300 mm and the width is 600 mm.
  16E: The drawer height is 400 mm and the width is 600 mm. 20E: The drawer height is 500 mm and the width is 600 mm.
  24E: The drawer height is 600 mm and the width is 600 mm.
The heights of common circuit breakers with different capacities are as follows:
  Molded case circuit breaker (MCCB) less than 250 A: 200 mm, occupying 8E (one drawer)
  400 A or 630 A MCCB: 400 mm, occupying 16E (two drawers)
  800 A MCCB: 600 mm, occupying 24E (three drawers)
Quantity of MCCBs installed in a low-voltage switch cabinet (for reference):
  Three 800 A MCCBs can be installed in a cabinet.
  Four 400 A or 630 A MCCBs can be installed in a cabinet.
  A maximum of nine 250 A or lower MCCBs can be installed in a cabinet.

## Slide 28: Example of Low-Voltage PDF Configuration (1)
The low-voltage side works in single bus mode and bus tie switches are configured. At any time, there are only two main inlet switches and bus tie switches are turned on.
Critical loads are powered by two supplies, two different transformers, and different buses.
Notes: Note that in a large-sized data center, different transformers are used for UPS loads and power loads to avoid mutual impact.

## Slide 29: Example of Low-Voltage PDF Configuration (2)
Cable entry cabinet: main cable entry ACB, 5000 A.
Cable outlet cabinet: 1250 A ACB, responsible for supplying power to chillers. One cable outlet cabinet can be installed with only two ACB.
Notes: Circuit breakers for chillers: 500000/0.8/380/1.732 = 950; Round up and select 1250 A circuit breakers.

## Slide 30: Example of Low-Voltage PDF Configuration (3)
Cable outlet cabinet: eight loops in total.
Calculate the capacity of low-voltage electric devices corresponding to different loads and the number of cables required, and then determine the PDF model based on the PDF space and current capacity.

## Slide 31
System Composition
Planning Preparation
Planning Method
  Planning Procedure
  Power Supply Solution Selection
  Low-voltage Electric Device Selection
  Low-Voltage PDF Configuration
  Conductor Selection

## Slide 32: Power Cable Selection
Common power cables in a data center include cables and busways.
A cable consists of copper cores, an insulation layer, and a jacket. Cables are classified into single-core cables, three-core cables, three-phase four-wire cables, and three-phase five-wire cables.
A busway consists of the conductive strip, protective shell, and connector box. It is used in scenarios with large calculated current and load density.
Feeder unit
Elbow
Connector box
Hanger
End plug
Straight section
Busway
cables
Notes: In the power distribution system of a data center, the conductor type is selected based on the load type, calculated current, and onsite conditions. For example, if the calculated current of a loop exceeds 400 A, the cross-sectional area of a common cable is too large and hard to install. In this case, the busway power supply solution should be chosen. In addition, if there are many terminal devices in the power distribution system, for example, dense loads in cabinets, the busway power supply solution is also suitable when factors such as economy and cabling space are considered. The busway solution is also a trend.

## Slide 33: Cable Selection Rules
The cable type (rigid or flexible and insulation layer type) is determined based on factors such as construction site characteristics, nature of power loads, and capacity. The cable specifications are determined based on the calculated current and the cable specifications provided by the manufacturer.
  Select the cable type based on the power supply mode. For single-phase power supply, use single-core or three-core cables. For three-phase power supply, use three-phase four-wire or three-phase five-wire cables.
  Select the corresponding cable cross-sectional area based on the calculated current according to the table of the current-carrying capacity of cables.
  Select the appropriate fireproof material of cables according to the requirement on data center reliability level. The fireproof material must comply with the American standard (NEC), European standard (IEC), or Chinese Ministry of Public Security standard (GA 306). In China, ZA-YJV, BVV, and RVV cables are generally used.
Notes: In a three-phase four-wire power distribution system, the current-carrying capacity of the N wire should be no less than the sum of the maximum unbalanced load current and harmonic current in the line. When the phase wire is not greater than 16 mm2 (copper) or 25 mm2 (aluminum), the neutral wire should have the same cross-sectional area as the phase wire. When the phase wire is larger than 16 mm2 (copper) or 25 mm2 (aluminum), if the neutral wire current is small, the N wire can have a smaller cross-sectional area than the phase wire but cannot be smaller than 50%. The current-carrying capacity table provided by the manufacturer generally takes phase wire selection into consideration. Therefore, select the cable type based on the current.
ZA-YJV: copper-core XLPE insulated PVC sheathed class A flame-retardant power cable

## Slide 34: Busway Selection Rules
The busway is applicable to the power supply and distribution system with a rated current of 250 A to 6300 A. The selection requirements are as follows:
  High protection level.
  When the calculated current of the loop is greater than 400 A, the busway power supply system is recommended.
  When terminal devices are densely deployed, busway power supply lines are recommended to improve reliability and reduce installation difficulties.
Notes: For example, if the operating current of a large-sized UPS exceeds 1000 A, a busway can be used to supply power from the main low-voltage PDF to the UPS PDF.

## Slide 35: Comparison Between the Cable and Busway Solutions (1)
Equipment
Cables
PDF
Equipment
Busway
Power distribution unit
Cable power distribution solution
Busway power distribution solution
Cables are routed separately and there are many loops. Each time a new device is added, cables need to be re-led from the PDF, causing many fault points.
Fewer loops and fault points, easy capacity expansion, and reduced total length of power supply paths.

## Slide 36: Comparison Between the Cable and Busway Solutions (2)
Item | Cable Solution | Busway Solution
Material cost | Relatively low | Relatively high
Installation mode | During cable installation, cable trays must be configured if cables are exposed. Trenches need to be dug for underground routing, which requires high construction costs. | Easy to install. Dedicated installation supports are provided.
Footprint | Cables with large diameters require a larger turning radius. | Elbows can be used at the turning of a busway, which occupies a small space.
Current-carrying capacity | Maximum current of a single cable: 400 A (VV type) | Maximum: 6300 A (intensive)
Circuit voltage drop | Large | Small
Service life | 10–15 years | ≥ 20 years
Solution design | Designed based on the power supply and distribution layout and does not need to be customized. | The design must be based on the floor plan. In addition, the site survey must be performed, and the straight section and elbow must be customized based on the site requirements.
Capacity expansion mode | Cannot be expanded. Cables need to be connected to the PDF again. | A branching loop can be added at the branch port.
Power transmission loss | High | Low

## Slide 37
System Composition
Planning Preparation
Planning Method
  Planning Procedure
  Power Supply Solution Selection
  Low-Voltage Electric Device Selection
  Low-Voltage PDF Configuration
  Conductor Selection

## Slide 38
(short-answer question) Why is reactive power compensation required for a data center?
Notes: 1. This is a requirement of the power company. The initial power factor of data center loads is generally less than 0.9. When the power is small, the quality of the power grid is affected because power consumption is large in data centers. When the power factor is small, the same power requires a larger current, and the line loss also increases. Therefore, reactive power compensation is required.

## Slide 40
V1R1
Chen Kaifeng/cwx377854
2019.01.25
Li Shaofeng/ l00486775
V5R2