## Slide 1: Data Center Diesel Generator System Planning

## Slide 2
The slides describe the diesel generator (DG) system planning for data centers, including the DG system requirement analysis, DG networking mode, DG model selection, DG capacity calculation, and fuel tank capacity calculation.

## Slide 3
On completion of this course, you will be able to:
  Get familiar with the DG system requirement analysis.
  Get familiar with the DG system networking modes.
  Master DG model selection.
  Master DG capacity calculation.

## Slide 4
System Composition
Planning Preparation
Planning Method

## Slide 5: System Scope
The following figures show the position of a DG subsystem in a power supply and distribution system.
High-voltage DG system
High-voltage DGs
Mains input
High-voltage PDF
Transformer
Medium-voltage PDF
Medium-voltage PDF
Medium-voltage PDF
Transformer
Medium voltage
chiller
Low-voltage PDF
DC power
Power PDF
Power PDF
Lighting
PDF
Other
AC array cabinet
DC array cabinet
Low-voltage chiller
UPS
UPS
Fans & Water
pumps
CRAC
Fire
extinguishing
Lighting
Low-voltage DG system
Low-voltage DG
Mains input
DC
power
Power PDF
Power PDF
Lighting
PDF
Other
High-voltage PDF
Transformer
Medium-voltage PDF
Transformer
Medium voltage
AC array
cabinet
DC array
cabinet
UPS
UPS
Fans & Water
pumps
CRAC
Fire
extinguishing
Low-voltage chiller
Lighting

## Slide 6: System Overview
A DG system is composed of a diesel engine, generator, control panel, fuel tank and so on.
DG exterior
Notes: Engine: a machine that converts a type of energy into another type of energy, usually chemical energy into mechanical energy. Sometimes it refers to a mechanical energy generation device. It can also refer to the entire machine including the mechanical energy generation device, such as a gasoline engine and an aeroengine. The engine was invented in England. The engine concept was also originated from English. Its original meaning is "an apparatus that produces mechanical energy."
Generator: It has many forms, but all operate according to the law of electromagnetic induction and electromagnetic force. Therefore, the general structure of the generator is as follows: Circuits and magnetic circuits that are inductive to each other are made of appropriate magnetic and conductive materials to generate the electromagnetic power and achieve the purpose of energy conversion.
Control panel: serves as an auxiliary device of the DG for users to operate and control the DG as well as set and view the operating parameters (voltage and frequency) and status of the DG. It consists of power distribution, mechanical energy, and signal ports.

## Slide 7
System Composition
Planning Preparation
Planning Method

## Slide 8: Planning Preparation - Requirement Analysis
Requirement analysis
  Data center tier: The data center tier determines the DG redundancy mode and DG operating mode (backup, limited-time running, or continuous running).
  Operating environment: altitude, ambient temperature and humidity, and indoor or outdoor environment
  Total load: The total load determines the DG type, capacity of a DG, and the number of DG.
Notes: The data center DG is generally a three-phase one. According to the reliability requirements, the running mode is backup/limited-time running/continuous running, and the redundancy mode is N, N+1, or 2N.
If the system reliability level is Uptime Tier I, select the N redundancy mode. If the system reliability level is Uptime Tier II or III, select the N+1 redundancy mode. If the system reliability level is Uptime Tier IV, usually select the 2N redundancy mode.
Select an appropriate voltage level and frequency based on the local voltage system. There are two voltage levels: high voltage (about 10 kV) and low voltage (about 0.4 kV).
Total load: Calculation based on the preceding information.

## Slide 9
Notes: Operating environment
  Indoor or outdoor: IP rating. If the DG is deployed outdoors, a high IP rating is required.
  Ambient temperature and humidity: The normal operating temperature of the DG ranges from –15°C to +40°C. If the temperature is beyond this range, protection measures must be taken for the DG. For example, if the temperature is low, auxiliary startup measures should be taken. The air humidity also affects the DG. If the DG is used in an environment with high air humidity for a long time, the DG will be greatly damaged or even cannot be used.
  Altitude: DG are used in places with an altitude lower than or equal to 1000 m. When the altitude exceeds 1000 m, the output power is derated. Higher altitude leads to lower local atmospheric pressure, thinner air, and lower oxygen content. As a result, the combustion condition of the DG deteriorates due to insufficient air intake.

## Slide 10
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  Networking Mode Selection
  DG Selection
  DG Capacity Configuration
  Fuel Tank Capacity Configuration

## Slide 11: Planning Procedure
Determine redundancy mode of the DG.
Choose the high-voltage or low-voltage DG.
Determine the working conditions: emergency backup/limited-time running/continuous running.
Calculate the capacity and number of DG based on the load type and capacity.
Determine the fuel tank capacity based on the backup time and hourly fuel consumption.
Fuel tank capacity configuration
DG capacity configuration
DG selection
Networking mode selection

## Slide 12
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  Networking Mode Selection
  DG Selection
  DG Capacity Configuration
  Fuel Tank Capacity Configuration

## Slide 13: Running Mode
 | Single Operating | Parallel Operating
Topology |  | 
Power range | Maximum power of a single DG: 3600 kVA | The power of parallel DG can reach 12 MVA or higher. (Theoretically, it can be infinite.)
Maintenance mode | DG can be maintained only when they are powered off. | DG can be maintained in turn, and power-off is not required.
Technical complexity | Easy to deploy due to simple control logics. | Difficult to deploy due to complex control logics. The voltage, frequency, and phase must be synchronous among parallel DG.
Applicable scenario | Medium- and small-sized data centers and large-size modular data center. | Large-sized data centers
Control panel
DG
Output circuit
breaker
Output PDF
Communications
cable
Power cable
Control
panel
DG
Output
circuit breaker
Parallel
cabinet/PDF
Control
panel
DG
Output circuit
breaker
Notes: Parallel operation requires auxiliary parallel cabinets, synchronization modules, load distribution modules, and air circuit breakers allowing fast switch-on.
Application scenario of the single operating solution
  A single DG supports a maximum capacity of 3600 kVA. If the low-voltage power distribution capacity is less than 3600 kVA, the single operating solution can be used. Then connect the DG output cabinet and transformer output cabinet to the low-voltage power distribution system through an ATS. The capacity of the single operating solution can meet the requirements of small- and medium-sized data centers. If the single operating solution can meet the power requirements of a large-sized modular data center, the single operating solution can be used. For systems with the same power, the cost of a single operating solution is lower than that of a parallel solution.
Application scenario of the parallel solution
  The maximum capacity of a parallel system is not limited. Non-modular large-sized data centers have high power supply requirements, and the single operating solution cannot meet the system capacity requirements. In this case, the parallel solution is required. For example, in the DG parallel solution of a data center, five 500 kVA DG are used to form a 4+1 system.

## Slide 14: Redundancy Mode (1)
 | N Solution (No Redundancy) | N+1 Solution | 2N Solution
Topology |  |  | 
Reliability level | The reliability is poor. The N solution meets the Uptime Tier Ⅰ requirements. | The reliability is favorable. The N+1 solution has one redundant DG and meets the Uptime Tier Ⅱ or Ⅲ requirements. | The reliability is high. The 2N solution has N redundant DGs and meets the Uptime Tier Ⅳ requirements.
DG maintenance | If any DG is being maintained, less than N DGs can be running. | DGs can be maintained one by one. | One group of N DGs can be maintained simultaneously.
Technical complexity | Technical complexity is low, and standalone running is applied. | Technical complexity is relatively high, and control logics need to be added to control the DG startup and stop. | Technical complexity is high, and the redundant N DGs can be standby or running simultaneously with the other N DGs.
Applicable scenario | Small-sized data center | Medium- and large-sized data center | Medium- and large-sized data center
N DG
Parallel output cabinets
N DG
Parallel output cabinets
1 redundancy
Notes: Application scenarios of the N solution (no redundancy)
  The DG configuration can meet the requirements of the system. When the mains supply fails, the N DG can supply power to key loads. However, the system has no redundancy, so it does not support online maintenance and has a single point of failure (SPOF). That is, if any DG stops running, the power requirement of N DG is not met. This solution applies to scenarios with low system availability, such as small-sized data centers. It meets the Uptime Tier I requirements.
Application scenarios of the N+1 solution
  The reliability of the N+1 solution is higher than that of the N solution. If the topology design is reasonable, the solution supports online maintenance. That is, if one DG is stopped as planned, the power requirement of N DG is not affected. This solution applies to medium- and large-sized data centers that require high reliability. The solution meets the Uptime Tier II requirements. If the line design is reasonable and online maintenance can be implemented, it will meet the Uptime Tier III requirements.

## Slide 15
Notes: Application scenarios of the 2N solution
  The 2N solution has the highest reliability. Sometimes, the 2(N+1) mode is used, which is similar to the 2N mode. In the 2N mode, dual power supplies are provided. All key loads are powered by dual power supplies. Therefore, the 2N mode can meet the fault tolerance requirements. That is, any single point of failure in the DG system does not affect the power requirement of N DGs. This solution applies to large-sized data centers that require high reliability. If the design is reasonable, the system can meet the Uptime Tier IV requirements.

## Slide 16: Redundancy Mode (2)
How can the following N+1 redundancy mode meet Uptime Tier Ⅲ requirements through cable connection design?
N DGs
Parallel output cabinets
1 redundancy
Notes: There are three control logics for a parallel DG system.
  Logic 1: After receiving the power failure signal, all DG are started at the same time. That is, no matter how much the load is, the N+1 DG connected in parallel always run at the same time.
  Logic 2: DG are started at the same time, and then cut off according to the load capacity.
  Logic 3: After receiving the power failure signal, the system starts only one DG and determines whether to start other DG based on the load capacity.
  The first control logic, that is, all DG are always online, is recommended for data centers. This mode prevents frequent DG startup and stop when the load capacity fluctuates rapidly. In addition, the internal resistance and impacts of harmonics can be reduced when multiple DG run at the same time, facilitating the stable running of the DG. The second control logic applies to scenarios where the load capacity changes slowly and this logic consumes least fuel. In the third control logic, DG are started in sequence, which is applicable to scenarios with small initial load and fixed load growth.

## Slide 17: Redundancy Mode (3)
In this mode, two paths are designed for the DG subsystems based on the N+1 DG solution.
Both the two solutions in the following figures meet Uptime Tier Ⅲ requirements. However, the cost of the solution on the right is lower compared with the solution on the left because at least two three-in-one DG cabinets can be saved.
In addition, two low-voltage bus tie switches are used to further improve the system reliability.
Two solutions that meet Uptime Tier Ⅲ requirements
Notes: On the premise that Uptime Tier III requirements are met, the solution on the right saves costs compared with the solution on the left. At least two three-in-one diesel generators and cabinets are not required.
The low-voltage bus tie switch is also adopted in the above two segments of low-voltage bus, so that the system reliability is further improved.
The low-voltage bus tie breakers are switched off when the two routes are normal. When one route has no mains supply, the mains input circuit breaker of this route is turned off first, and then the bus tie switch is turned on. In this way, one route bears all loads.

## Slide 18
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  Networking Mode Selection
  DG Selection
  DG Capacity Configuration
  Fuel Tank Capacity Configuration

## Slide 19: High- or Low-Voltage DG Selection (1)
DG are classified into low-voltage (0.4 kV) and high-voltage (10 kV) DG based on the output voltage. Except the output voltage varied with the DG configuration, the two types of DG have basically the same engine, control system, and technology.
No. | Comparison | Low-Voltage DG (0.4 kV) | High-Voltage DG (10 kV)
1 | DG cost | 1 | 10% to 15% higher
2 | Installation cost | Same | Same
3 | Cooling mode | Same | Same
4 | Noise control | Same | Same
5 | O&M | Same | Same
6 | Footprint | Basically the same | Basically the same
7 | Grounding system | Not required | A ground resistance cabinet is required.
8 | Efficiency | Same | Same
9 | Startup time | Same | Same
Comparison between low- and high-voltage DGs

## Slide 20: Medium- or Low-Voltage DG Selection (2)
No. | Comparison | Low-Voltage DG (0.4 kV) | High-Voltage DG (10 kV)
10 | Auxiliary switch cabinet | 0.4 kV | 10 kV
11 | Power transmission medium | Low-voltage power cable or bus | High-voltage power cable
12 | Power transmission cost | High | Low
13 | Power transmission loss | High | Low
14 | Power transmission distance | Near (less than or equal to 150 m) | Far (less than or equal to 2000 m)
15 | Non-linear load bearing capability | The DG is directly connected to a load and is easily affected by a non-linear load. | In most cases, a transformer is used for connecting a load, and the transformer can eliminate part of the impact of a non-linear load on the DG.
Comparison between low- and high-voltage DG

## Slide 21: Medium- or Low-Voltage DG Selection (3)
No. | Comparison | Low-Voltage DG (0.4 kV) | High-Voltage DG (10 kV)
16 | Load power factor | The DG is directly connected to a load and is easily affected by the load power factor. | In most cases, a transformer is used for connecting a load to avoid that the output power of the DG is affected by an excessively low power factor.
17 | Parallel operating | The parallel capacity is small because the DG is limited by the current of the low-voltage power distribution device. | High-power DG can be connected in parallel to form a large-capacity system.
18 | Switching to the mains supply | ATS with a bypass are used, and this requires large current and multiple ATS, resulting in a large footprint and high costs. | A comprehensive control switch can be installed on the 10 kV bus to control the switchover, and this requires a small footprint and low costs.
Comparison between low- and high-voltage DG

## Slide 22: Medium- or Low-Voltage DG Selection (4)
Due to the performance limitation of low-voltage electrical equipment, the capacity of a single or parallel low-voltage DGs cannot exceed 2400 kW. If the total capacity of low-voltage DGs in a small- and medium-sized data center is less than 2400 kW and less than 10 DGs are connected in parallel, the 0.4 kV DG is preferred. Otherwise, the 10 kV DG is preferred.
Uptime Tier | Recommended DG Redundancy Mode | Remarks
Tier I | N | A single DG is recommended and the capacity cannot exceed 2400 kW.
Tier II | N+1 or 2N | If the total capacity of DG does not exceed 2400 kW and less than 10 DG are connected in parallel, the low-voltage DG solution is recommended. Otherwise, the high-voltage DG solution is recommended.
Tier III | N+1 or 2N | Same as above
Tier IV | 2N | Same as above

## Slide 23: Voltage Mode Selection
The following table lists the voltage levels of the low- and high-voltage DG.
DG voltage level
Low Voltage (Three-Phase/Single-Phase) |  | High Voltage (Three-Phase) | 
50 Hz | 60 Hz | 50 Hz | 60 Hz
380/220 | 416/240 | 10500 | 12470
400/231 | 440/254 | 11000 | 13200
415/240 | 460/266 | 6300 | 13800
440/254 | 480/277 | 6600 | 3300
 |  | 6900 | 4160
Notes: DG should be selected based on the local power supply modes. In China, the power supply mode is 220/380, 50 Hz.

## Slide 24: DG Power Selection
Determine the nominal power of the DG in a data center based on factors such as the mains reliability and data center reliability requirements. If the requirements are excessively high, for example, the consecutive power (COP) is used, the cost increases. If the requirements are excessively low, for example, the emergency standby power (ESP) is used, the reliability is decreased.
Note:
  For Uptime Tier Ⅲ and Tier Ⅳ data centers, COP DG are required.
  For Uptime Tier Ⅰ and Tier Ⅱ data centers, LTP- or PRP- DG can be used.
Notes: Output power ratings of DG:
  COP: Continuous power (COP)-rated DG supply the maximum power continuously to constant loads for an unlimited number of hours annually. COP-rated DG are suitable for power plants.
  PRP: Prime power (PRP)-rated DG supply the maximum power continuously to variable loads for an unlimited period of time annually. The 24-hour average load power is less than or equal to 70% of the PRP. PRP-rated DG often reserve extra speed adjustment power and can run at 10% overload. However, the average load rate, allowed full-load running time, and overload running time for different power plants vary. PRP-rated DG are applicable to industrial or civil engineering scenarios where the mains supply is unavailable or poor.
  LTP: DG rated as limited-time running power (LTP) supply the maximum power for 500 hours annually. LTP-rated DG have no requirements on the load rate and are applicable to the areas with reliable mains supply.
  ESP: Emergency standby power (ESP)-rated DG supply the maximum power to a variable load for 200 hours annually. The 24-hour average load power is generally less than or equal to 70% of the ESP. ESP-rated DG are applicable to common offices, real estate, and other places that do not have high reliability requirements.
  When the preceding four types of power are calibrated for the same DG, the ratio of the calibrated power is about ESP:LTP:PRP:COP = 1000:920:850:780.

## Slide 25
Notes: The preceding definition is based on ISO 8528-1:2005. Generally, the nominal output power on the nameplate of a DG consists of the standby power, primary power, and continuous power. The standby power refers to the maximum power with which a DG can run continuously for 300 hours within the specified maintenance period and under the specified environment conditions. The DG should be able to run at the maximum power for 500 hours per year. The standby power is equivalent to the LTP in ISO standards. The prime power is the maximum power of a variable power sequence with which a DG can run for an unlimited number of hours each year in the specified maintenance period and under the specified environment conditions. The prime power is equivalent to the PRP in ISO standards. The consecutive power is the maximum power of a constant power sequence with which a DG can run for an unlimited number of hours each year in the specified maintenance period and under the specified environment conditions. The consecutive power is equivalent to COP in ISO standards. However, the definition and standards of power rating vary among different vendors. Therefore, you need to consult the vendor to determine during model selection.

## Slide 26
Notes: Generator power supply site:
In Uptime Tier III or IV data centers, the engine generator system, its power path, and other auxiliary components shall meet the requirements for parallel maintenance and/or fault-tolerance performance verification tests.
Runtime limit
Engine generators at Uptime Tier III and IV data centers shall not have a limit on continuous operating time on the premise that the load meets the N requirement. Engine generators with limits on continuous operating hours are suitable for Tier I or II data centers. Only continuous operating power or derated prime rate meets the TIER III and IV requirements.

## Slide 27: DG Selection Summary
After the DG model is determined, the following information should be provided:
  DG power: COP/LTP/PRP
  DG voltage level: high/low voltage
  DG power supply mode: 50/60 Hz, 400 V/480 V/11,000 V...

## Slide 28
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  Networking Mode Selection
  DG Selection
  DG Capacity Configuration
  Fuel Tank Capacity Configuration

## Slide 29: DG Capacity Configuration (1)
Capacity of a DG:
  PICT is the total ICT load.
  PHVAC is the total load of the heating, ventilating, and air conditioning (HAVC) system (air controlling devices).
  Pe is the load of other systems, such as the lighting system and building management system (BMS).
  K1 is the load coefficient. The value depends on many factors, such as the UPS battery charge power, startup power for air controlling devices, and reliability factor. K1 is normally 1.4.
  K is the environment coefficient, which is related to the temperature and altitude. K is 1 by default. It decreases by 3% to 4% as the temperature increases by 5°C when the environment temperature exceeds 40°C, and decreases by 4% to 5% as the altitude increases by 500 m when the altitude exceeds 1000 m.
Notes: The capacity is an estimation value.

## Slide 30: DG Capacity Configuration (2)
Determine the DG model, capacity, and quantity based on the list provided by the manufacturer.
Cummins DG capacity
Model
Standby
Load (kVA)
Constant
Load (kVA)
Engine Model
Standby
Load (kVA)
Constant
Load (kVA)
Notes: Note: The preceding figure shows part of power segments.

## Slide 31: Configuration Example
According to the load statistics of an Uptime Tier III data center, the IT load is 700 kW, the power load is 800 kW, and the lighting load is 60 kW.
According to the formula:
The total required power is calculated as follows: (700 + 800) x 1.4 + 60 = 2160 kW
Because this is a Tier Ⅲ data center. Therefore, COP-rated DG is required. The following uses C1675 D5A as an example:
  N solution: 2
  N+1 solution: 2+1
  2N solution: 2 x 2
Standby
load (kVA)
Standby
load (kW)
Constant
load (kVA)
Constant
load (kW)
Notes: The reason why the active power is used for calculation is that the reactive power can be met in most cases.
Only one model is used as an example. In actual model selection, parameters such as the cost and model size also need to be considered.

## Slide 32
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  Networking Mode Selection
  DG Selection
  DG Capacity Configuration
  Fuel Tank Configuration

## Slide 33: Fuel Tank Capacity Configuration (1)
DG fuel storage requirements of data centers at all levels
Notes:
  For a Tier Ⅲ or above data center, the fuel tank must be redundant. Except the fuel in the redundant fuel tank, the remaining fuel must be able to support 12-hour operation of N DG.
  For a Tier Ⅲ or above data center, the fuel pipeline also needs to be designed in a similar way as the chilled water pipeline. The 2N design, loop design, or dual-pipe design can be adopted.
Level Standard | Tier Ⅳ | Tier Ⅲ | Tier Ⅱ | Tier Ⅰ
Uptime | 12 hours | 12 hours | 12 hours | No specific requirements
TIA-942 | 96 hours | 72 hours | 24 hours | /
Notes: For a Tier III or above data center, the fuel tank must be redundant. Except the fuel in the redundant fuel tank, the remaining fuel must be able to support 12-hour operation of N DGs.
  Assume that there are three DGs in a 2+1 system. The system stores fuel for 12-hour operation. A total of 3000 liters fuel are required, and each DG requires 1000 liters. Therefore, at least two 2000-liter fuel tanks are required, and one of them is standby.

## Slide 34: Fuel Tank Capacity Configuration (2)
Fuel tank capacity calculation
  V = g·t/γ/a = v·P·t/a
    V: volume of the daily fuel tank (m3); g: fuel consumption (kg/h) of the DG, which can be obtained from the product brochure.
    γ: fuel density (kg/m3), 810–860 kg/m3 for light diesel; a: fullness coefficient of the fuel tank. Generally, the value is 0.90.
    t: fuel supply time. Generally, the value is 3 to 8 hours. The value depends on the customer's requirements and is restricted by the specifications.
    v: fuel consumption (L/kWh) of the DG, which can be obtained from the product brochure.
    P: power (kW) of the DG.
  In addition to the preceding calculation result, calculate the capacity of the daily fuel tank based on the diesel fuel consumption required for the trial operation in the normal refueling period.
Notes: The capacity of a fuel tank is designed based on the fuel consumption of the DG at full load. Generally, a less than 500 kW DG is equipped with a daily fuel tank that is installed at the bottom of the DG and it can provide fuel for the DG running for 8 to 12 hours at full load. An additional daily fuel tank needs to be installed for a big-power DG. When the customer requires an additional fuel tank, note that the capacity of the daily fuel tank in the DG room cannot exceed 1000 liters according to the fire protection regulations. The daily fuel tank of the standby DG is set to run at full load for 8 hours according to the communications industry standards. Therefore, a separate fuel tank room is required if the capacity exceeds 1000 liters, and fire extinguishing facilities are required according to the related fire protection regulations.
V: Generally, the fuel consumption of a DG ranges from 0.2 L/kWh to 0.35 L/kWh. In the initial planning, 0.3 L/kWh can be used for capacity estimation.

## Slide 35: Fuel Tank Capacity Configuration (3)
If the fuel reserve of the daily fuel tank cannot meet the requirement for power backup time, a large fuel tank or underground fuel depot needs to be installed outdoors.
Calculation of outdoor fuel tank capacity:
  Vtotal tank volume = V – Vdaily total volume
  Vtank = Vtotal tank volume/(N·a)
  where:
    Vtotal tank volume: calculated total capacity of outdoor fuel tanks (m3); V: calculated total capacity (m3).
    Vtank: calculated capacity of the outdoor fuel tanks (m3); N: number of fuel tanks.
    a: fullness coefficient of the fuel tank. The value is usually 0.9 for the diesel fuel used for the data center.

## Slide 36: Fuel Tank Pipeline Configuration (1)
Uptime Tier Ⅲ application:
  Similar to the chilled water pipeline design, the 2N, loop, or dual-pipe design can be adopted.
  The fuel reserve must support 12-hour operation of N DG (daily fuel tank + reserve fuel tank).
  For a Tier Ⅲ or above data center, the fuel tank must be redundant. Except the fuel in the redundant fuel tank, the remaining fuel must be able to support 12-hour operation of N DG.
  In this solution, there are two sets of fuel pipes and fuel pumps, but the pipes and routes are not isolated.

## Slide 37: Fuel Tank Pipeline Configuration (2)
Uptime Tier Ⅳ application:
  Typically, Tier Ⅳ data centers adopt 2N DG solution. If a DG room is to be constructed, two DG must be physically isolated and not be placed in the same room.
  The 2N pipeline design is the simplest, and the two pipelines are completely isolated. No pipes should be deployed between the two main fuel tanks. In addition, there must be some distance between the two pipeline systems so that the fault of one pipeline does not affect the other.
2N pipeline design
Notes: After the fuel tank is configured, the DG planning is complete, and the other components are easy to configure.
  Controller selection
    If there is no specific requirement, select the controller provided by the DG manufacturer or a third-party controller. The controller needs to be compatible with the existing devices, and supports manual control mode and multi-language operations.
  Parallel device selection
    If multiple DG are running in parallel, select the corresponding parallel device.
    For example, the Cummins DG is equipped with a parallel device by default. You only need to configure one parallel cabinet. A parallel cabinet and parallel device need to be installed for the Caterpillar DG to implement the parallel function.

## Slide 38
Notes:   Other components
    Select the soundproof canopy based on the customer's requirements. If the customer does not have specific requirements, the soundproof canopy is designed based on 85 dB per meter of the equipment room.
    Select a startup battery string and battery charger to ensure the normal startup of the DG. The VLRA batteries are usually selected. The voltage of the startup motor is 12 V or 24 V. Select a compatible battery string. You can also configure batteries in 2N mode to meet reliability requirements.
  Other precautions
    The DG must comply with local certification, such as the safety regulation certification and environment protection certification.
    The following safety regulation and environment protection certifications are usually needed: CE and RoHS certifications in the EU, UL certification in the North America, and 3C certification in China.

## Slide 39
System Composition
Planning Preparation
Planning Method
  Planning Method Overview
  Networking Mode Selection
  DG Selection
  DG Capacity Configuration
  Fuel tank configuration

## Slide 40
（T or F）The operation time of DG used in an Uptime Tier Ⅲ or above data center should not be restricted.
（T or F）The redundancy mode of DG used in an Uptime Tier Ⅲ or above data center should be N+1 or 2N and that the power supply paths of the DG support online maintenance or fault tolerance.
Notes: 1. True
2. True

## Slide 42
Chen Kaifeng/cwx377854
2020.4.
Li Shaofeng/ l486775
New