## Slide 1: Solution Analysis for the Data Center Power Distribution System

## Slide 2
The slides describe the typical power distribution solutions for different levels of data centers and their applications, including the working logic, application scenarios, advantages and disadvantages of these solutions. The slides also describe how to improve these solutions.

## Slide 3
On completion of this course, you will be able to:
  Get familiar with the working logic of different power distribution solutions in a data center.
  Analyze the advantages of different power distribution solutions in a data center.
  Identify the disadvantages of different power distribution solutions in a data center.

## Slide 4
Typical Solutions
Solution Application Analysis

## Slide 5: Reference Solution for an Uptime TierⅠData Center
Single power supply and distribution route, diesel generator (DG), non-redundant uninterruptible power system (UPS)
If any device on the power distribution route is faulty or overhauled, the service system may break down.
This architecture is applicable to data centers used by small-sized enterprises that do not have specific requirements on service continuity.
Power distribution topology of a Tier Ⅰdata center
AC PDF
AC PDF
Notes: One mains input is used in all the solutions mentioned in the slides. The high-voltage mains input is not displayed.

## Slide 6: Reference Solution for an Uptime Tier Ⅱ Data Center
Single power supply and distribution route, N+1 DG, UPS, and cooling devices.
Faults and maintenance of key components do not affect the running of service devices.
Faults and maintenance of the power supply and distribution route will affect the running of service devices.
This architecture is applicable to data centers used by small- and medium-sized enterprises and aggregation sites of carriers that have no specific requirements on service continuity.
Power distribution topology of a Tier II data center
AC PDF
AC PDF
AC PDF
Notes: If the customer has high reliability requirements and IT loads use dual power supplies, the power supply route from the UPS to the IT devices can adopt dual power supplies to improve system reliability. However, the topology is still at the Tier II level.

## Slide 7: Reference Solution for an Uptime Tier Ⅲ Data Center (1)
Active-active power supply routes, 2N DG, and 2N UPS.
Dual power supplies for cooling devices.
Architecture with active-active routes and 2N DG
AC PDF
AC PDF
AC PDF
AC PDF
Route A
Route B
LV panel
Notes: The construction cost of Tier I/II equipment rooms is low, and the facility reliability is low. The facility of Tier IV equipment rooms is highly reliable, but the construction cost is high.
Tier III equipment rooms have a good balance between construction costs and facility reliability and are widely deployed as important equipment rooms in various industries. The power supply architecture of a Tier III equipment room is also diversified.
The following analyzes typical power supply topologies for Tier III data centers that are commonly used in the industry.
Notes:
  The Uptime standard does not require continuous cooling for Tier III equipment rooms. However, the construction certification has requirements on the temperature rise (the temperature change is less than or equal to 5°C/15 minutes) of the equipment room when the mains supply is disconnected and the DG is started. To ensure that the customer's service equipment does not break down, continuous cooling must be configured in the chilled water cooling scenario and direct expansion (DX) cooling scenario with the power density of 5 kW or higher per cabinet.

## Slide 8
Notes: Notes:
  In the following recommended architectures, DX air conditioners are used in the cooling system for illustration purpose. In the chilled water scenario, continuous cooling is implemented by deploying a chilled water tank as well as chilled water pump and air conditioner indoor unit powered by the UPS.
  One mains input is used in the example.
This solution meets the Tier IV requirements in terms of the power supply architecture. The only difference lies in whether physical route isolation is required in the actual construction process.
This solution is costly but highly reliable.

## Slide 9: Reference Solution for an Uptime Tier Ⅲ Data Center (2)
Active-active power supply routes, N+1 DG, and 2N UPS.
Dual power supplies for cooling devices.
Active-active parallel DG routes.
Type A architecture with active-active routes and N+1 DG
AC PDF
AC PDF
AC PDF
AC PDF
Route A
Route B
Notes: The difference between this solution and the previous solution is that the DG is in N+1 mode, which can reduce the cost. However, the system still uses active-active routes.

## Slide 10: Reference Solution for an Uptime Tier Ⅲ Data Center (3)
Active-active power supply routes, N+1 DG, and 2N UPS.
Dual power supplies for cooling devices.
Backup DG shared by routes A and B.
Type B architecture with active-active routes and N+1 DG
AC PDF
AC PDF
AC PDF
AC PDF
Non-critical load
Route A
Route B
Notes: This solution is basically the same as the previous solution. However, the internal architecture of the DG is optimized to meet the reliability requirements and reduce the cost.
Working logic: DG 1 and DG 3 carry loads A and B respectively. DG 2 is a standby DG and does not work. If DG 1 or DG 3 is faulty, DG 2 starts. During the standby DG starts, the load is carried by the UPS.
Compared with type A architecture (based on the topology analysis), this solution requires two fewer three-in-one DG parallel cabinets and two fewer output power distribution cabinets for each DG. If the system scale is large, hundreds of thousands of US dollars can be saved.

## Slide 11: Reference Solution for an Uptime Tier Ⅲ Data Center (4)
Multiple active power supply routes, DG and UPS route redundancy. The routes provide two power supplies for terminal devices in hand-in-hand mode.
Complex O&M management, applicable to low-cost scenarios.
DR architecture
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
Route A
Route B
Route C
Notes: In this solution, loads are divided into N (3 in this example) parts. The loads should be large enough to be divided into N parts. Therefore, this solution applies to large-sized data centers.
Each part of loads adopts active-active routes, which ensures high load reliability. When one power supply route is faulty, its loads are switched to the other two routes, and the air conditioner on the faulty route uses single power supply. However, the cost of this solution is lower than that of the solutions 1 and 2 for Tier III data centers. According to preliminary calculation, the UPS redundancy is lower than 2N. The 2N solution requires N redundancy. In this solution, the total capacity of the UPS here is 1.5 N, and the redundancy is 0.5 N.
The disadvantage is that the maintenance is complex and there are many loops. During maintenance, you need to determine which route (A, B, or C) the loads are from. In addition, when adding new servers, you need to evenly distribute the load to each route to avoid adding all loads to only one route.

## Slide 12: Reference Solution for an Uptime Tier Ⅲ Data Center (5)
Active-active power supply routes, N+1 DG, and N+1 UPS; one HVDC and one mains supply for servers
This architecture applies only to cloud data center scenarios with high power supply quality.
Architecture with active-active routes, one HVDC, and one mains supply
AC PDF
AC PDF
AC PDF
AC PDF
Route A
Route B
Notes: In this solution, the server needs to be customized to support one HVDC input and one mains input, and the mains quality must be good because the mains is directly supplied to the power module of the loads. If the mains quality is poor, the power module will be damaged. Mains in China, Japan, Europe, and the United States can meet the requirements, but the mains quality in Southeast Asia is poor.
In addition, the data centers must be cloud data centers. In China, such data centers are generally used by China Mobile, China Unicom, and China Telecom as well as Baidu, Alibaba, and Tencent (BAT). The reliability of this power supply solution is relatively low and needs to be supplemented by the IT side. If some faults occur in the cloud data centers, processes and services are automatically migrated and virtualization technologies are used; therefore only some services will be affected by power failure.

## Slide 13: Reference Solution for an Uptime Tier Ⅲ Data Center (6)
Active-standby power supply routes, N+R DG, and N+R UPS.
Single power supply for loads.
Applicable only to cloud data centers.
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
IT LOAD 1#
IT LOAD N#
Route 1
Route N
Standby route
Standby DG
Standby UPS
Standby A/C UPS
N+R architecture with active-standby routes
Notes: The redundancy or backup mentioned in this solution is route-level backup. For example, the loads shown in the figure are divided into two parts (can be three, four, or N theoretically). Each part has an independent transformer, DG, UPS, and PDF to meet the load requirements. The route on the right is standby. The R is the standby route. You can determine the capacity of the standby route based on the actual requirements. The cost depends on whether only one load or all loads need to be backed up.
This solution needs to be distinguished from the previous DR solution. Although the loads of the two solutions are partitioned, the entire power supply architecture is different. The power supply routes of the DR architecture are multiple active power supply routes, and the downstream loads use two power supplies, and the two power supply routes carry loads. However, in this solution, only the active route carries loads, and the other route is used as a backup and carries loads only during active route maintenance.
This solution is also applicable to cloud data centers.

## Slide 14: Reference Solution for an Uptime Tier Ⅲ Data Center (7)
The loads are categorized into N identical modules. Each module is configured with independent 2N UPS, a DG, a transformer, and 2N power distribution routes.
Each module shares the redundant DG.
Applicable to 2 MW or higher data centers.
Architecture with pseudo active-active routes sharing the redundant DG
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
AC PDF
Route A
Route B
Route B
Standby DG
Route A
Notes: In this solution, loads are evenly divided into N parts. Therefore, this solution is applicable to large-sized data centers. In 2 MW or higher data centers, loads need to be partitioned.
Every N loads are configured with an independent DG, transformer, 2N UPS, and 2N power supply routes. For a Tier III data center, the DG must be redundant. Therefore, the DG in the middle is a backup DG shared by the entire data center. The DG is connected to route A of each load module, and route B is connected through the ATS.
All the preceding topologies comply with the Uptime Tier III requirements. However, in actual application, there may be a slight change. For example, if the low-voltage power distribution bus has dual inputs, a bus tie switch needs to be added. However, the main architecture remains unchanged.

## Slide 15: Comparison of Tier Ⅲ Power Supply Topologies
Now we use an actual project model (300 cabinets, 1.7 MW) to compare the costs, reliability, and maintainability of different power distribution architectures.
Architecture | Reliability | Cost | Maintainability | Scenarios
Architecture with active-active routes and 2N DG | Highest | A | Easy maintenance | Recommended if only two DG are used in the project
Type A architecture with active-active routes and N+1 DG | 5-Star | 0.958A | Easy maintenance | /
Type B architecture with active-active routes and N+1 DG | 5-Star | 0.884A | Easy maintenance | Preferred for 2 MW or lower data centers
DR architecture | 5-Star | 0.790A | Complex maintenance | Preferred in scenarios with tight budgets
Architecture with active-active routes, one HVDC, and one mains supply | 4-Star | 0.856A | Easy maintenance | Cloud data centers with good power grid quality
N+R architecture with active-standby routes | 3-Star | 0.754A | Complex maintenance | Cloud data centers
Architecture with pseudo active-active routes sharing the redundant DG | 4.5-Star | 0.951A | Easy maintenance | Scenarios with power greater than 2 MW
Notes: Notes:
  Assume that the high-voltage power distribution of each architecture, load power distribution, and the backup time of the project system are the same. The architecture cost comparison involves only the transformer, transformer output cabinet, DG, DG output cabinet and parallel cabinet, low-voltage switching cabinet, UPS, UPS input cabinet, UPS output cabinet, and mains PDF.
  If the customer requires the single-side backup time be the same, the costs of the architecture with active-standby routes, architecture with active-active routes, architecture with one HVDC and one mains, and N+R architecture with active-standby routes can be further reduced because half of backup batteries are saved.
  The pseudo active-active routes share the redundant DG, which is not applicable to scenarios with less than 2 MW power. Therefore, the cost is high for this project.
Type A architecture with active-active routes and N+1 DGs requires fewer DG output cabinets and parallel cabinets. Therefore, the cost is further reduced, but the reliability remains unchanged. Only three DGs are required in this project. If the power is greater than 1.8 MW, there will be a DG price surge. Therefore, this architecture is preferred for 2 MW or lower data centers.

## Slide 16
Notes: DR architecture: The cost will be further reduced because the redundancy lowers, but the maintenance becomes complex. Therefore, the DR architecture is recommended only when the budget is tight.
Active-active routes architecture with one HVDC and one mains routes: The cost is basically the same as that of the architecture of active-standby routes. The main difference is the contact switch.
N+R architecture with active-standby routes: This architecture is least reliable because the redundancy of the backup is low. If the redundancy is high, the cost is high. In addition, the maintenance is complex, but it is simpler than the DR architecture. This architecture is recommended in cloud data centers.

## Slide 17: Reference Solution for an Uptime Tier Ⅳ Data Center
Active-active routes, 2N DG/UPS/cooling devices
All devices and power distribution routes in the active-active routes are physically isolated (excluding service devices).
A fault of any component on one route does not affect the normal running of the other route or service devices.
AC PDF
AC PDF
AC PDF
AC PDF
Route B
Route A
Notes: The power supply architecture for a Tier IV data center uses active-active power supply routes, 2N redundancy of DG, UPS, and cooling devices, as well as continuous cooling of the cooling system (DX scenario: The air conditioners are configured with the UPS; water-cooled scenario: The chilled water tanks, chilled water pumps, and air conditioner indoor units are configured with the UPS). All devices and power distribution routes in the active-active routes are physically isolated (excluding service devices). A fault of any component on one route does not affect the normal running of the other route or service devices. This architecture is applicable to scenarios that have high requirements on service continuity, such as central data centers of banks and core equipment rooms of carriers.

## Slide 18
Typical Solutions
Solution Application Analysis

## Slide 19: Case 1 (1)
Power distribution solution for PL data center
Transformer station
10 kV power
distribution device
Cabinet
Load
Transformer
PDU
1000 kVA x 1
4 kW x 50
100 kVA x 2
Transfer from 110 kV
to one 10 kV input cable
Precision air
conditioner A
Other loads
DG
400 V DG power
distribution panel
Two (1+1) 800 kVA DGs
Automatic DG startup and switching
DG
Active
Standby
Precision air
conditioner B
UPS
UPS
PDU
100 kVA x 2
UPS
UPS
200 kW
200 kW
Note: 200 kW is the cooling capacity of the air conditioners.
120 kVA x 2
120 kVA x 2
ATS

## Slide 20: Case 1 (2)
Discussion:
  Which tier of requirements does the power supply solution meet?
    Consider the following aspects:
      DG configuration
      Transformer configuration
      UPS configuration
      Power supply route for loads
  How to improve the reliability of the power distribution solution by one tier?
    No new main devices such as the UPS, transformer, and DG should be added, but the ATS and low-voltage power distribution frame (PDF) can be added.

## Slide 21: Case 1 (3)
Which tier of requirements does the power supply solution meet: Tier Ⅱ
  DG configuration: 1+1
  Transformer configuration: N
  UPS configuration: 2N
  Power supply route for loads: pseudo dual power supplies
  In conclusion, core components, such as the DG and UPS, meet the N+1 or higher requirements. The power supply route is pseudo dual power supplies. Although the transformer is configured in N mode, the Uptime standard does not have requirements on the mains.

## Slide 22: Case 1 (4)
Solution 1 example: Add the following configuration:
  An ATS
  A low-voltage PDF
  A DG parallel cabinet
  A transformer one-to-two PDF
Cabinet
Load
PDU
Precision air
conditioner A
Transformer station
10 kV power distribution device
Transformer
DG
Parallel
cabinet 1
DG
Precision air
conditioner B
UPS
UPS
PDU
UPS
UPS
Parallel
cabinet 2
Low-voltage
PDF A
Low-voltage
PDF B
ATS
ATS

## Slide 23: Case 2 (1)
Transformer
station 1
Transformer
station 2
10 kV power
distribution device
10 kV power
distribution device
DG
UPS
UPS
Cabinet
Load
10 kV DG parallel system
Transformer
Transformer
Transformer
Transformer
PDU
...
PDU
Six (5+1) 2250 kVA DG
...
DG
DG
...
UPS
UPS
...
...
...
...
10.5 MVA
UPS
Chilled water
pump
Precision air
conditioner
ATS
Chiller
Cooling
water
pump
Cooling tower
...
Other
power
loads
Other
power
loads
...
Chiller
Cooling
water pump
Cooling
tower
UPS
ATS
...
ATS
ATS
Different physical routes
10.5 MVA
Circuit breaker status:
On
Off
Power distribution solution for LZ data center
Notes: High-voltage side:
  The two 10 kV mains inputs use different physical routes, and the high-voltage power supplies are connected through bus tie switches, which further improves system reliability. The 10 kV high-voltage DG system is used. Note that the high-voltage DG is connected to the mains bus through a circuit breaker, and the low-voltage DG is connected to the mains bus through an ATS. The DG is configured in N+1 mode, but there is only one route. This is a risk point.
Low-voltage side:
  Power loads and IT loads are configured with independent transformers. Low-voltage bus tie switches are configured between routes A and B to improve system reliability.
  IT loads are powered by UPS in dual-loop mode.
  In terms of cooling, continuous cooling is also considered. The chilled water pump and air conditioners are configured with UPS. For the devices that use single power supply, the ATS is used to switch the route. The chiller, cooling water pump, and cooling tower use dual power supplies controlled by a terminal ATS.
  Other power loads are powered by a single mains supply.

## Slide 24: Case 2 (2)
Discussion:
  Which tier of requirements does the power supply solution meet?
    Consider the following aspects:
      DG configuration
      Transformer configuration
      UPS configuration
      Power supply route for loads
  What are the advantages and disadvantages of this solution?
  How to add configurations to improve system reliability?

## Slide 25: Case 2 (3)
The power supply solution complies with the requirements for Uptime Tier Ⅱ data centers.
  DG configuration: N+1 (5+1), there is only one DG route.
  Transformer configuration: 2N
  UPS configuration: 2N
  Power supply route for loads: dual power supplies
    In conclusion, except for the DG route, other routes meet online maintenance requirements. However, the data center tier is determined by the weakest route.
Notes: After a parallel cabinet is added to the DG system, the architecture is similar to the Type A architecture with active-active routes and N+1 DG. This architecture is widely used in large-sized data centers.

## Slide 26: Case 2 (4)
Advantages:
  Dual mains supplies in active-active mode are used. Bus tie switches are configured on the high- and low-voltage sides to improve the reliability of the mains.
  The DG is configured in N+1 mode. When both mains inputs are faulty, the DG start, improving system reliability.
  On the load side, the IT devices are powered by two routes, and the UPS is configured in 2N mode. The loads such as chillers and cooling towers are powered by two routes, which are controlled by a terminal ATS. IT loads and power loads are isolated to avoid mutual impact.
  Chilled water pumps and air conditioners are also powered by two routes controlled by a terminal ATS. But one route is from an independent UPS to achieve continuous cooling.
Disadvantage:
  There is only one route on the DG side.

## Slide 27: Case 2 (5)
Add a DG parallel cabinet to form a dual-route system, improving the system reliability.
Common DG configurations for Tier Ⅲ data centers
DG A
Transformer A
DG B
Transformer B
Low-voltage
PDF A
DG A
DG B
Transformer
2N DG, two
mains supplies
2N DGs, one mains supply
Transformer A
Transformer B
Transformer
N+1 DG, two mains supplies
N+1 DG, one mains supply
Low-voltage
PDF A
Low-voltage
PDF B
Low-voltage
PDF B
Low-voltage
PDF A
Low-voltage
PDF A
Low-voltage
PDF B
Low-voltage
PDF B
Note: Low-voltage DG are used here. The architectures are the same for high-voltage DG.

## Slide 28: Case 3 (1)
UPS
UPS
Cabinet
load
0.4 kV DG parallel system
T2
T4
UPS
T5
T6
Chilled
water pump
Precision air
conditioner
ATS
Cooling
water pump
PDU
...
PDU
Three (3+0) 2000 kW DGs
...
1#
Chiller
Cooling water
pump
Cooling tower
Other
power loads
2#
Chiller
Cooling water
pump
Cooling tower
UPS
ATS
ATS
UPS
UPS
...
...
10 kV power
distribution device
10 kV power
distribution device
ATS
ATS
ATS
ATS
Test load
T1
T3
Test load
Mains 1
Mains 2
Power distribution solution for WH data center
Notes: Dual mains inputs. The low-voltage DG and mains are switched over by the ATS on the low-voltage side.
Terminal load:
  IT loads are powered by two power routes. Cooling loads are powered by two routes controlled by a terminal ATS. Continuous cooling is configured. Chilled water pumps and precision air conditioners are powered by two routes controlled by a terminal ATS. One route is from an independent UPS.

## Slide 29: Case 3 (2)
Discussion:
  Which tier of requirements does the power supply solution meet?
    Consider the following aspects:
      DG configuration
      Transformer configuration
      UPS configuration
      Power supply route for loads
  What are the advantages and disadvantages of this power supply solution?
  How to improve the system reliability?

## Slide 30: Case 3 (3)
The power supply solution complies with the requirements for Uptime Tier Ⅰ data centers.
  DG configuration: N (3+0)
  Transformer configuration: 2N
  UPS configuration: 2N
  Power supply route for loads: dual power supplies
  The configuration of the DG system is N. The tier of the power distribution system is determined by the weakest route.
Notes: Although this solution complies with the requirements for Uptime Tier I data centers, it complies with class B requirements according to the Chinese GB standard. Because the mains quality in China is good, so the importance of DGs is weakened. Uptime is a global standard. The mains supply is poor in Southeast Asia, Africa, and Middle East. Therefore, the importance of DGs is highlighted.

## Slide 31: Case 3 (4)
Advantages:
  Dual mains supplies in active-active mode are used. Bus tie switches are configured on the high- and low-voltage sides to improve the reliability of the mains.
  The DG is configured in N mode. When both mains inputs are faulty, the DG start, improving system reliability.
  On the load side, the IT devices are powered by two routes, and the UPS is configured in 2N mode. The loads such as chillers and cooling towers are powered by two routes, which are controlled by a terminal ATS. IT loads and power loads are isolated to avoid mutual impact.
  Chilled water pumps and air conditioners are also powered by two routes controlled by a terminal ATS. But one route is from an independent UPS to achieve continuous cooling.
Disadvantages:
  N configuration on the DG side severely reduces system reliability.
  Using a low-voltage DG causes complex power supply routes, excessive ATS applications, and complex control.

## Slide 32: Case 3 (5)
How to improve the system reliability?
  Use high-voltage DG. In this way, the number of ATS is greatly reduced, and the control logic is simplified.
  Change the configuration on the DG side to N+1 and add DG routes if necessary to improve system reliability.
Notes: Pay attention to the differences between the high-voltage DG and low-voltage DG in actual applications.

## Slide 33: Case 4 (1)
Transformer
station1
Transformer
station2
Transformer
Transformer
Transformer
Transformer
UPS
Chilled water
pump
Precision air
conditioner
ATS
Chiller Cooling
water pump
Cooling tower
Chiller Cooling
water pump
Cooling tower
ATS
...
ATS
ATS
10 kV power
distribution device
10 kV power
distribution device
UPS
Cabinet
load
PDU
...
UPS
UPS
...
...
UPS
DG
DG parallel room A
DG
DG
DG parallel room B
DG
DG
PDU
Five (4+1) 2200 kVA DGs
Power distribution solution for BF data center

## Slide 34: Case 4 (2)
Discussion:
  Which tier of requirements does the power supply solution meet?
    Consider the following aspects:
      DG configuration
      Transformer configuration
      UPS configuration
      Power supply route for loads
  What are the advantages of this power supply solution?

## Slide 35: Case 4 (3)
The power supply solution complies with the requirements for Uptime Tier Ⅲ data centers.
  DG configuration: N+1 (4+1)
  Transformer configuration: 2N
  UPS configuration: 2N
  Power supply route for loads: dual power supplies

## Slide 36: Case 4 (4)
Advantages:
  Dual mains supplies in active-active mode are used. Bus tie switches are configured on the high- and low-voltage sides to improve the reliability of the mains.
  The DG is configured in N+1 mode. When both mains inputs are faulty, the DG start, improving system reliability.
  On the load side, the IT devices are powered by two routes, and the UPS is configured in 2N mode. The loads such as chillers and cooling towers are powered by two routes, which are controlled by a terminal ATS. IT loads and power loads are isolated to avoid mutual impact.
  Chilled water pumps and air conditioners are also powered by two routes controlled by a terminal ATS. But one route is from an independent UPS to achieve continuous cooling.

## Slide 37: Case 5 (1)
Transformer station1
10 kV power distribution device
Transformer
5+1 medium-voltage
DG system
Transformer station 2
10 kV power distribution device
Low-voltage power distribution
UPSA1
Output power distribution
Precision PDF
rPDU1
rPDU1
Server A
Transformer
Low-voltage power distribution
UPSA2
Output power distribution
Precision PDF
rPDU1
rPDU1
Server B
Low-voltage power distribution
UPSA6
Output power distribution
Precision PDF
rPDU1
rPDU1
Server C
Transformer
...
4 routes in total
Low-voltage power distribution
UPSB
Output power distribution
Precision PDF
Transformer
...
3 routes in total
Two DG
routes
Power distribution solution for LX data center
Notes: The system works in N+R route-level backup mode. A1 to A6 are active routes, and B is a standby route.
The capacity of Route B can be 1 to N according to the budget or requirement.

## Slide 38: Case 5 (2)
Discussion:
  Which tier of requirements does the power supply solution meet?
    Consider the following aspects:
      DG configuration
      Transformer configuration
      UPS configuration
      Power supply route for loads
  What are the advantages of this power supply solution?

## Slide 39: Case 5 (3)
The power supply solution complies with the requirements for Uptime Tier Ⅲ data centers.
  DG configuration: N+1
  Transformer configuration: N+R
  UPS configuration: N+R
  Power supply route for loads: active-standby routes
Advantages:
  IT loads are powered by two routes (one active and one standby) and can be maintained online as planned.
  Compared with the traditional UPS 2N configuration, this configuration reduces costs.
Notes: Disadvantages: Although IT loads use dual power supplies, the power supplies are not active-active. The reliability is lower than that of the traditional UPS 2N configuration. The cost is reduced, but the reliability is also reduced.

## Slide 40
Typical Solutions
Solution Application Analysis

## Slide 41
（T or F）The power supply architecture of a data center is as follows: dual mains supplies, 2N transformers, 2N UPS, and N+1 diesel generators. The diesel generators share one combiner cabinet, and the loads are cofigured with dual-paths power supply. The power supply solution of the data center meets the requirements of an Uptime Tier Ⅲ data center.
Notes: 1. F

## Slide 43
V1R1
Chen Kaifeng/CWX377854
2020.4
Li Shaofeng/l486775
V5R2