## Slide 1: Data Center Power Distribution Solution Optimization

## Slide 2
The slides describe how to optimize a data center power distribution solution. We have learned that a data center power distribution solution should be reliable and simple. In this training, we will optimize the data center power distribution solution from these two perspectives.

## Slide 3
On completion of this course, you will be able to:
  Get familiar with the operation modes of different power distribution solutions for data centers.
  Analyze the advantages and disadvantages of different power distribution solutions for data centers.
  Identify and optimize the weaknesses of different power distribution solutions for data centers.

## Slide 4: Trainee Grouping
Steps for trainee grouping
  Before the training, the trainer prepares the same number of poker cards as the number of trainees. Every three cards have the same number.
  Trainees draw lots before the training and those who draw the cards with the same number form a group.
  If the number of trainees is excessive, the trainer specifies the group to which the excessive trainees belong.
  Each group assigns its group name.

## Slide 5: Import
Task description:
  What are the basic requirements for the power distribution system of an Uptime Tier Ⅲ data center?
Task execution rules:
  Each group discusses the question for 5 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.
Notes: The UPS system in the figure is not redundant.

## Slide 6: Answer
Data centers that can be concurrently maintained have redundant capacity components and multiple independent power distribution routes to serve critical systems. At any time, only one distribution route is required to serve the critical environment.
All IT devices use dual power supplies and are properly installed to be compatible with the data center architecture topology. If the critical environment does not meet this specification, a transmission device such as a switch must be used.
Onsite fuel reserve should support 12-hour operation of N diesel generators (DGs).

## Slide 7: Case 1
Carrier XX needs to reconstruct its data center to meet the Uptime Tier Ⅲ requirements.
Engineer C is the power distribution solution designer of the general contractor. The figure on the right shows the original power distribution solution.
In the solution:
  There is one mains input and N DGs.
  UPS 1 is configured in N mode, and IT load 1 uses single power supply.
  UPS 2 is configured in N+1 mode, and IT load 2 uses dual power supplies.
  UPS 3 and UPS 4 have the same capacity and each can support IT load 3. IT load 3 uses dual power supplies.
  The air conditioners in all rooms are direct expansion air-cooled air conditioners with dual power inputs. The configuration is N+1.
ATS
DG
Mains
Main PDF
PDB
PDB
PDB
UPS2
UPS1
UPS3
UPS4
IT load 1
IT load 2
IT load 3
PDF
PDF
PDF
PDF
PDF
AC1
AC2
AC3
Power distribution solution
Equipment room 1
Equipment room 2
Equipment room 3

## Slide 8: Task 1
Task description
  The original power distribution solution can meet the requirements of Uptime Tier ___ data centers. Specify reasons.
Task execution rules
  Each group discusses the question for 10 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.
ATS
DG
Mains
Main PDF
PDB
PDB
PDB
UPS2
UPS1
UPS3
UPS4
IT load 1
IT load 2
IT load 3
PDF
PDF
PDF
PDF
PDF
A/C1
A/C2
A/C3
Power distribution solution
Equipment room 1
Equipment room 2
Equipment room 3

## Slide 9: Answer to Task 1
The original power distribution solution meets the requirements of Uptime Tier Ⅰdata centers.
Reason:
  The DG is configured in N mode.
  UPS 1 is configured in N mode, and IT load 1 is powered by a single route, which may cause a single point of failure.
  The data center tier is determined by the weakest route. Therefore, this solution can only meet the requirements of Uptime Tier I.

## Slide 10: Task 2
Task description
  After discussing with the customer, engineer C determines a new solution.
    Considering the increase of services, one DG is reused and two new DGs are added to form 2+1 configuration. The mains supply is still one route.
    The UPS system is configured in 2N mode. UPS 3 and UPS 4 are reused to supply power to loads in equipment room 3. UPS 1 and UPS 2 are replaced with new ones.
    All air conditioners are reused, but continuous cooling is required. Add a set of UPS 5 to supply power to the air conditioners.
  Based on the preceding information, change the original power distribution solution to a solution that meets the requirements of Uptime Tier Ⅲ.
Task execution rules
  Each group discusses the question for 15 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.

## Slide 11: Answer to Task 2
ATS
Mains
Main PDF
UPS3
UPS4
IT load 3
PDF
PDF
New power distribution solution
DG 1
DG 2
DG 3
Parallel cabinet 1
Parallel cabinet 2
Main PDF
ATS
A/C2
UPS5
A/C1
IT load 2
UPSA
UPSB
IT load 1
PDF
PDF
A/C3
PDB
STS

## Slide 12: Background of Case 2
The XX data center needs to be reconstructed so that it can pass the Uptime Tier Ⅲ certification.
Engineer Z from the general contractor is responsible for designing the power distribution system solution. Engineer Z provides the power supply topology as shown in the following figures.
  Note: IT load 1 has a single power supply, and IT loads 2 and 3 have dual power supplies.
Mains
High-voltage PDF
ATS
ATS
DG: 2 x 1500 kVA
S1
S2
DG: 1 x 1500 kVA
ATS
S3
S1
Chiller
S3
ATS
S2
S3
UPS1
UPS2
PDF1
PDF2
IT load 1
IT load 2
PDF3
PDF4
IT load 3
Power supply topology
The UPS system is configured in N mode.
The DG system is configured in N+1 mode.
Notes: Note:
This solution does not cover the mains input. The scope is from the transformer to the load. The upstream of the transformer is not displayed here.

## Slide 13: Task 1
Task description
  Does the original solution meet the Uptime Tier Ⅲ requirements? Specify the reasons.
Task execution rules
  Each group discusses the question for 15 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.
Mains
High-voltage PDF
ATS
ATS
DG: 2 x 1500 kVA
S1
S2
DG: 1 x 1500 kVA
ATS
S3
PDF1
PDF2
IT load 1
IT load 2
S1
Chiller
S3
ATS
PDF3
PDF4
IT load 3
Power supply topology
S2
S3
UPS1
UPS2
The UPS system is configured in N mode.

## Slide 14: Answer to Task 1
The original solution does not meet the Uptime Tier Ⅲ requirements.
Reason
  The power supply route does not meet concurrent maintenance requirements.
    IT load 1 has a single power supply, and a single point of failure exists.
    Although IT load 2 and IT load 3 have two power supplies, there is only one route from the UPS to the low-voltage PDF, and a single point of failure also exists.
  Key capacity devices do not meet redundancy requirements.
    The DG system is configured in N+1 mode, and the UPS does not have sufficient redundancy.
Notes: The original power distribution solution can only meet the Uptime Tier I requirements.

## Slide 15: Task 2
Task description
  Reconstruct the power distribution solution and make it meet the Uptime Tier Ⅲ requirements.
    Step 1: Determine the power distribution reconstruction solution from the UPS to IT loads. The UPS system should be a dual-bus system. The PDFs are reused, and the number of circuit breakers is sufficient.
    Step 2: Determine the power distribution reconstruction solution from the mains to the UPS. The DG system is reused and configured in 2+1 mode, the one mains input remains unchanged, and the transformer is reused.
Task execution rules
  Each group discusses the question for 20 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.
Notes: Note: There is no standard answer for this solution. The answer is right as long as the configuration is reasonable and meets the Tier III requirements. The cost is not considered.

## Slide 16: Answer to Task 2 (1)
Power distribution solution from the UPS to IT loads: 2N UPS configuration
UPS1
UPS2
PDF1
PDF2
IT load 1
IT load 2
PDF3
PDF4
IT load 3
The UPS system is configured in N mode.
IT load 1
IT load 2
IT load 3
PDF3
PDF4
PDF1
PDF2
STS
UPSA
UPSB
The UPS system is configured in 2N mode.
Original power distribution solution
After the reconstruction

## Slide 17: Answer to Task 2 (2)
Mains
High-voltage PDF
ATS
DG: 1 x 1500 kVA
S1
DG: 1 x 1500 kVA
ATS
S2
S1
Chiller
S2
ATS
S1
S2
UPSA
UPSB
DG: 1 x 1500 kVA
Parallel cabinet
Parallel cabinet
Mains
High-voltage PDF
ATS
ATS
DG: 2 x 1500 kVA
S1
S2
DG: 1 x 1500 kVA
ATS
S3
S1
Chiller
S3
ATS
S2
S3
UPS1
UPS2
Original solution
After the reconstruction
Power distribution solution from the upstream mains to the UPS

## Slide 18: Task 3
Task description
  Determine an appropriate UPS and battery configuration solution based on the power distribution solution and load capacity in the previous task.
    Note:
      The capacity of IT loads 1, 2, and 3 is 250 kW, 500 kW, and 450 kW.
      The capacity of a single UPS can be 100 kVA, 200 kVA, 300 kVA, 400 kVA, 500 kVA, or 600 kVA. The output power factor is 1, the IT load power factor is 0.9, and the battery backup time is 15 minutes.
      The battery capacity does not need to be calculated.
Task execution rules
  Each group discusses the question for 15 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays the results and
  explains the calculation process in sequence.
  The trainer makes a summary.
IT load 1
IT load 2
IT load 3
PDF3
PDF4
PDF1
PDF2
STS
UPSA
UPSB
Notes: Note: There is no standard answer for this task. The answer is right as long as the configuration is reasonable and meets the Tier III requirements. The cost is not considered.

## Slide 19: Answer to Task 3
UPS configuration
  UPS capacity = (250 + 500 + 450)/0.9 x 1.2 = 1600 kVA.
  Two sets of 3 x 600 kVA or two sets of 4 x 500 kVA UPSs can be selected.
  Two sets of 3 x 600 kVA UPSs can be selected to reduce costs.
Battery configuration
  Each UPS is connected to separate batteries. The backup power of each UPS is calculated as follows: (250 + 500 + 450)/3 = 400 kW. The backup time is 15 minutes with constant power.
  If either route A or route B is faulty, the backup time can still meet the requirements.
Notes: It is recommended that a maximum of four UPSs be connected in parallel.

## Slide 20: Background of Case 3
Company XX needs to build a new data center. Engineer L is the data center architect of the general contractor and is studying the power distribution solution provided by the customer.
The customer requires that the data center must pass the Uptime Tier Ⅲ certification.
ATS1
Parallel cabinet
Chiller
ATS2
Parallel cabinet
PDF1
PDF2
ATS3
ATS4
Precision air conditioner
ATS
UPS1
UPS2
STS4
STS3
Load
STS2
STS1
Load
UPS3
G
G
G
Original power supply topology
The UPS system is configured in N+1 mode.
The UPS system is configured in N+1 mode.
Mains 1
Mains 2
The DG system is
configured in 2+1
mode.
Notes: This solution does not cover the mains input. The scope is from the transformer to the load. The upstream of the transformer is not displayed here.
Mains 1 and 2 come from different transformer stations.

## Slide 21: Task 1
Task description
  Discuss whether the power supply topology meets the Uptime Tier Ⅲ requirements and describe the basis.
Task execution rules
  Each group discusses the question for 15 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.

## Slide 22: Answer to Task 1
The power supply topology complies with the Uptime Tier Ⅲ requirements.
Reason:
  The DG is configured in N+1 mode, and N is 2.
  Power load: The precision air conditioner supports continuous cooling. One route is from the UPS, and the other route is from the mains. Chillers use dual power supplies controlled by an ATS at the end.
  IT load: Two power supplies are provided. The UPS is configured in N+1 mode. The two inputs of the IT loads are from two STSs respectively. One of the two STS inputs is from the UPS, and the other is from the mains. The mains are from different transformers, improving reliability.
  In conclusion, the key capacity facilities are configured in N+1 mode. In addition, the dual power supply routes are used, which supports concurrent maintenance and meets the requirements of Uptime Tier Ⅲ data centers.

## Slide 23: Task 2
Task description
  Discuss whether the solution can be optimized without affecting the data center tier (Uptime Tier Ⅲ). If yes, draw the optimized power distribution diagram and explain the reasons.
  Requirements: The DG system is still configured in 2+1 mode, and the UPS is in 2N mode.
Task execution rules
  Each group discusses the question for 30 minutes.
  Write the discussion result on the electronic whiteboard.
  Each group displays and explains the results in sequence.
  The trainer makes a summary.

## Slide 24: Answer to Task 2
This solution can be optimized.
Bus-tie
Chiller
Parallel cabinet
Parallel cabinet
PDFA#
Precision air conditioner
UPSA#
Load
PDFB#
UPSB#
Bus-tie
PDFC#
PDFD#
UPS3
G
G
G
Power supply topology after optimization
ATS1
ATS2
ATS3
ATS4
Mains 2
Mains 1
Mains 1
Mains 2
Notes: Note:
There is no standard answer. The answer is right as long as it is reasonable.
There are two mains inputs. The transformers and UPSs are configured in 2N mode. A bus tie switch is added between transformers to improve reliability.
IT loads and power loads are configured separately to minimize mutual impact.

## Slide 25: Answer to Task 2
Disadvantages of the original solution:
  Excessive redundancy and use of the ATS and STS greatly increase the cost and complicate the operation and maintenance.
  There are multiple mains and transformers, but the IT loads and power loads are not separated.
Optimization
  Separate IT loads and power loads, and ATS1 and ATS2 at the downstream of the transformers do not need to be configured.
  All loads use dual power inputs. All STSs can be omitted by optimizing the UPS solution.

## Slide 26: Summary of Task 2
Although this architecture fully meets the requirements of Uptime Tier Ⅲ, it is too complex and difficult to maintain. In addition, too much redundancy is used, resulting in high costs.
Uptime Tier Ⅲ requirements are not rigid, but flexible.
The core requirement of Uptime Tier Ⅲ is as follows:
  "All power distribution devices are concurrently maintainable without affecting the normal running of the data center." This requirement is result-oriented and does not require a specific power distribution architecture. The core requirement can be met as long as concurrent maintenance is realized.

## Slide 27
In this chapter, we have learned how to analyze the power distribution solution of data centers on the live network, including new data centers and reconstructed data centers, from two aspects: reliability and simplicity.
First, ensure that the solution is reliable. On the premise that the reliability requirements are met, make the solution as simple as possible. If the solution is too complex, the O&M work will be complex, and the system reliability will be affected in another way.

## Slide 29
Chen Kaifeng/cwx377854
2020.9.30
Li Shaofeng/l486775
New