## Slide 1: Data Center Cooling System Planning

## Slide 2
A data center construction project can be large or small, new or refurbished, and complete or partial.
The project may involve changes in the physical area of the equipment room, equipment layout, or electrical capacity, power density increase, and redesign of the power or cooling architecture. Regardless of the scale or nature of the project, the success of a project depends not only on the procurement and installation of physical system equipment, but also on the entire planning and design process from project concept to commissioning.
This course describes the process and implementation of the cooling system project planning, including the planning process, precautions, and requirements.

## Slide 3
On completion of this course, you will be able to:
  Master the cooling system planning process of a data center.
  Master the requirement planning of a data center cooling system.
  Master the cooling system planning of a data center.

## Slide 4
Data Center Cooling System Planning Introduction
  Data Center Cooling System Planning, Design, and Life Cycle Overview
  Data Center Planning Process
Implementation of the Data Center Cooling System Planning Process

## Slide 5: Planning and Design of a Data Center Cooling System
  A new data center is built.
  The cooling architecture is changed.
  From centralized cooling to in-row cooling
When do I need to start the planning and design of a data center cooling system?
Risks occur.
  In addition, when a data center is upgraded or needs to be re-planned or coordinated, some devices need to be shut down or isolated. In this case, the adaptation of the cooling system needs to be considered.
  The air supply mode is changed to underfloor air supply.
Notes: Many scenarios are involved. Main scenarios include construction and reconstruction. Other cases are special and need to be analyzed based on actual conditions.

## Slide 6: Phases in the Life Cycle of a Data Center Cooling System
Planning and design
Planning lays a key foundation for future work of the project.
Raising requirements
Evaluating requirements
Establishing preliminary design requirements
System planning
Determining design
Preparations
Onsite coordination
Assembling
Startup and
running
Commissioning
Use training
O&M
Troubleshooting
Requirement planning
Solution design phase
Evaluation
Construction and commissioning
O&M and evaluation
Notes: Planning is the most likely to cause confusion, misunderstanding, and communication errors. The mistakes made in the planning phase will be further amplified and spread in the subsequent construction phase. Typical consequences are delay, restart, cost overruns, time waste, and frustration, which will ultimately affect system performance.

## Slide 7
Data Center Cooling System Planning Introduction
  Data Center Cooling System Planning, Design, and Life Cycle Overview
  Data Center Planning Process
Implementation of the Data Center Cooling System Planning Process

## Slide 8: Input for Requirement Planning
Facility requirements
Total cooling capacity
Spatial layout
Scalability
Power density
Standards and specifications
Project requirements
Requirement planning
Determine the reliability level of a data center cooling system based on the importance of services.
Estimate the IT device power, space, power, and cooling requirements when the data center is fully loaded to determine the total cooling capacity.
Analyze the space planning requirements of the data center to be constructed, and preliminarily discuss and determine the spatial layout.
Predict the requirement change and growth of cooling throughout the entire life cycle of a data center in the future based on the scalability requirements.
Requirement determination
Process
Notes: The final requirement consists of the following elements:
  Standard requirements usually appear in the form of standards and specifications (main components of data center specifications). Examples of standard requirements include special regulatory compliance standards, subsystem compatibility, safety, or best practices that need to be publicly explained to engineers or installers.
  Project requirements define the details of project execution for users.

## Slide 9: Cooling System Requirement Planning Process
Determine project specifications.
Tier requirement: Refer to data center specifications, such as Uptime, GB 50174, and TIA-942. Pay special attention to service types on the customer side.
Capacity requirement: The maximum IT load supported by the data center physical infrastructure (DCPI) is determined by the IT side.
Power density: Whether cabinets with high, medium, or low power density are considered.
Energy efficiency requirements: Currently, the PUE recommended by the Chinese GB standard is lower than 1.4.
Future plan: The future development plan of a data center is divided into several phases.
Budget: from the budget plan of the overall project
Consider special requirements and restrictions.
Analyze and refer to existing documents to optimize project specifications.
From requirement input
Key specifications
Initial solution
selection
Special requirements
and restrictions
Obtain project materials that are similar to the preceding six project elements. Compare the materials with the six elements and use the comparison result as the basic input source of the solution.
Reference design includes the following key indicators: overall IT load, power supply and cooling redundancy, and power density.
Recommended sources: Reference solutions are obtained by end users and data center operators, or from mature DCPI suppliers such as Huawei and Schneider.
Consider special requirements and restrictions.
Notes: Determine project specifications: Hold meetings with related personnel and other personnel who understand the core service requirements and objectives to determine macro objectives of the data center project and determine basic requirements for the DCPI.
Initial solution selection: Obtain some basic specifications from previous mature projects in the industry in advance as a reference, use them as the basis of the solution, and then adjust the solution based on the preferences or restrictions of specific users.
Consider special requirements and restrictions: Special requirements refer to customers' special requirements. Restrictions are determined by the environment and are not controlled by the data center designer. Restrictions include facility restrictions, regulatory restrictions, or unchangeable service requirements. Professional consultants are required to assess whether decisions affecting the physical location of facilities comply with related national and regional standards.

## Slide 10
Notes: The industry suggests that the final requirements consist of the following elements:
  Standard requirements, which do not change with the project. Standard requirements usually appear in the form of standards and specifications (main components of data center specifications). Examples of standard requirements include special regulatory compliance standards, subsystem compatibility, safety, or best practices that need to be publicly explained to engineers or installers.
  Project requirements define the details of project execution for users. These include special deadlines, allocation or limitations of human or equipment resources, and mandatory special procedures or other management processes that must be followed by suppliers or the project.
Requirement planning must be performed by the customer. The planned budget is the project budget, excluding the operating expense (OPEX) budget.
Preference refers to expectations that users may change or adjust after considering (or re-considering) costs and results. Sometimes, user preferences change after the user gets new information.
Restrictions are conditions that cannot be overcome or will incur great costs or cause unacceptable consequences if not observed. Restrictions are pre-existing conditions that are difficult or impossible to change.

## Slide 11: System Planning Analysis Input of a Data Center
Based on comprehensive analysis and evaluation of multiple factors, adjust and modify the plan and complete the planning of the cooling system type, overall layout, and preliminary plane partition of a data center.
System planning
All contents of requirement planning must be provided. The selected cooling system must meet the requirements for cooling space, power supply, safety, floor load, grounding, and electrical protection.
The system planning involves the layout and technology selection of the computer room area, support area, auxiliary area, and other areas.
Plan the phased principle and subsequent implementation plan. The subsequent implementation should not affect the operation of completed areas.

## Slide 12: Cooling System Planning Process
Obtain and prepare for tasks.
  Task scenario analysis
  Floor plan
  Modular layout planning
  Typical layouts and requirements of different levels
Check the detailed planning data of the system.
  Cooling load determination
  Indoor unit determination
  Feasibility study solution output
3
1
2
Determine the system solution.
  Cooling source solution planning
  Energy-saving solution planning
  Indoor unit solution planning
  Humidity measurement and control planning
  Fresh air system solution planning
Feasibility study report output

## Slide 13
Data Center Cooling System Planning Introduction
Implementation of the Data Center Cooling System Planning Process
  Requirement Planning
  System Planning

## Slide 14: Determining Key Planning Specifications that Affect the Cooling System
Expected average and peak power consumption of cabinets
and information about the uncertainty of power density
  Describes the growth period of a data center, including uncertain factors.
System level requirements to be met based
on industry standards and specifications
  Planned capital cost for the project
Maximum IT load (kW)
supported by the DCPI
  DCPI energy efficiency target. PUE is
  one of the common indicators.
Power density
Budget
Future plan
Energy
efficiency
requirement
Capacity
requirement
Level
requirement
Six project specifications

## Slide 15: Considering Special Requirements and Restrictions
Collect and evaluate special requirements of users:
  We want top cabling.
  We want to make visitors feel comfortable when they visit the site.
  We hope that surveillance cameras can monitor the data center cooling system.
  We prefer wide IT cabinets to obtain more cabling space.
  We want to physically separate IT cabinets for different IT customers.
  ...
Discuss the issues one by one, draw a definite conclusion, and release the conclusion.
Notes: In most cases, multiple modifications are required to determine the final user preferences and restrictions. This task is completed when preferences and restrictions are adapted to system concepts and summarized as conceptual adjustments, validated preferences, and validated restrictions. If user preferences and restrictions are synchronized with the previous task, the process and task can be completed more quickly. Note that many restrictions cannot be determined before the location is selected. This may require the previous task of developing system concepts to be performed before you can collect restrictions.
The main idea here is that user preferences and restrictions should be adjusted to fit the system concepts that have been chosen.

## Slide 16: Considering Special Requirements and Restrictions
Restrictions
  Physical properties of facilities (ceiling height, floor bearing capacity, geometric shape of the equipment room, existing columns or walls, rooftop installation requirements for outdoor equipment, and onsite pipe routing requirements)
  Local laws or regulations
  Physical properties of the transportation passage (such as the bearing capacity of the elevator for transporting equipment to the equipment room)
In this example, one cabinet position is occupied.
A column can occupy a maximum of three cabinet positions based on the column dimensions and the position of the column in the cabinet row.
Removing several cabinets in the middle of the cabinet row will cause mixing of cold and hot air.
Deployment scenario 1
Deployment scenario 2
Hot aisle
Cold aisle
Hot aisle
Cold aisle
Cold aisle
Hot aisle
Cold aisle
Hot aisle
Cold aisle
Cold aisle

## Slide 17
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 18: Data Center Reconstruction(1)
For many projects, an equipment room already exists. You need to deploy devices in the equipment room. Generally, you need to perform site survey to obtain the building information and device layout.
Take the international LAN switch room of an airport building as an example. The following operations need to be performed:
  Understand the reconstruction scope, including the number and types of customer cabinets in the equipment room to define the project scope.
  Record the equipment room information: The total area of the equipment room is 280 m2.
  Record the cabinet information: There are 100 cabinets in 10 rows to be reconstructed. The distance between each row is 1 m; the height of a cabinet is 2.2 m and the width is 0.6 m; the total power consumption of the cabinets is 80 kW; the distance between the top of the cabinets and the air duct is 0.9 m; the position of the column is marked.
Racks not to be reconstructed
Racks not to be reconstructed
Front side
Cable trough cabinet
  Record the power supply and distribution of the cooling system in the equipment room, the cooling planning of the equipment room, the original indoor and outdoor units of air conditioners, water supply, fresh air, and air exhaust in case of faults in the equipment room.
  Obtain the onsite drawing from the customer or draw a drawing onsite.
Notes: Purpose: To calculate the load of the air conditioning system, determine the system mode, plan the device installation position, and plan the pipe layout. The device power must be the actual power of the cabinet. If nameplate power is used, the calculated cooling load will be higher than the actual value.

## Slide 19: Data Center Reconstruction(2)
After selecting a solution, you need to perform the following operations:
  Obtain geographic and climatic information.
  Calculate cooling load (cooling loss).
  Obtain the cooling capacity of indoor units.
  Consider measurement tolerance and energy consumption.
  Determine the pipe routing mode of the indoor units of air conditioners.
  Confirm other requirements, including heater (dehumidifier), humidifier, teamwork control, fire extinguishing linkage, water leakage interruption, DCIM remote monitoring and control, and maintenance space.

## Slide 20: Impact of Site Selection on a Cooling System – Climate(1)
Climate
A data center requires cooling throughout the year. In areas where the ambient temperature is low throughout the year, free cooling can be used to reduce the compression cooling time, saving energy and reducing costs. However, the cost of heating and humidification may increase in very cold areas. Comprehensive analysis needs to be performed for different areas.
Chart: Shanghai
| 完全自由冷却 | 部分自由冷却 | 电制冷
 | 695 | 2532 | 5533
Chart: Ordos
| 完全自由冷却 | 部分自由冷却 | 电制冷
 | 4249 | 2035 | 2476
Chart: Beijing
| 完全自由冷却 | 部分自由冷却 | 电制冷
 | 2930 | 1741 | 4089
Chart: Wuhan
| 完全自由冷却 | 部分自由冷却 | 电制冷
 | 747 | 2467 | 5546
Chart: Guangzhou
| 完全自由冷却 | 部分自由冷却 | 电制冷
 | 0 | 1017 | 7743

## Slide 21: Impact of Site Selection on a Cooling System – Climate(2)
Area | Indicator |  | Requirement
 | Key Indicator | Auxiliary Indicator | 
Severe cold area | Average temperature in the coldest month: ≤ –10°C | Number of days when the daily average temperature is lower than or equal to 5°C: ≥ 145 days | Heat preservation requirements in winter must be fully met. Generally, protection measures against heat in summer can be ignored.
Cold area | Average temperature in the coldest month: 0°C to –10°C | Number of days when the daily average temperature is lower than or equal to 5°C: 90–145 days | Heat preservation requirements in winter should be met. Protection measures against heat in summer in some areas should be considered.
Mild area | Average temperature in the coldest month: 0–13°C; average temperature in the hottest month: 18–25°C | Number of days when the daily average temperature is lower than or equal to 5°C: 0–90 days | Heat preservation requirements in winter in some areas should be met. Generally, protection measures against heat in summer can be ignored.
Areas with hot summer and cold winter | Average temperature in the coldest month: 0°C to –10°C; average temperature in the hottest month: 25–30°C | Number of days when the daily average temperature is lower than or equal to 5°C: 0–90 days; number of days when the daily average temperature is greater than or equal to 25°C: 40–110 days | Protection measures against heat in summer must be taken. Heat preservation in winter should be considered based on requirements.
Areas with hot summer and warm winter | Average temperature in the coldest month: > 10°C; average temperature in the hottest month: 25–29°C | Number of days when the daily average temperature is greater than or equal to 25°C: 100–200 days | Protection measures against heat in summer must be taken. Generally, heat preservation in winter can be ignored.
Direct ventilation free cooling days

## Slide 22: Impact of Site Selection on a Cooling System – Air Quality
Air quality
The corrosion mechanism of air contaminants on IT equipment is complex. Corrosion is usually caused by multiple contaminants. International standards for the pollution degree are often set using silver and copper test bars (measuring the thickness of corrosives every month, which is usually 200 angstroms using silver bars and 300 angstroms using copper bars).
The site must be away from dust, oil fume, harmful gas, or corrosive, flammable, or explosive materials. (Sea and landfills are also sources of corrosive materials.)
Occasional air pollution may also cause damage to servers.
Exercise caution when selecting direct ventilation free cooling. Even if there is no contaminant temporarily, the air quality may be affected in the future.
Mountain fires, autumn harvests, salt fields, hazardous chemical explosions can all be sources of pollution.

## Slide 23: Impact of Site Selection on a Cooling System – Environmental Factors
Do local utility conditions, such as electricity, water supply and drainage, communications, diesel, and heat, meet the requirements of a data center?
Are there any building restrictions, noise restrictions, contaminant emission restrictions, and other local government restrictions?
Is there an annual power outage maintenance time period that is not recognized by the planned maintenance?

## Slide 24
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 25: Influence of a Floor Plan on Cooling Planning of Data Centers
Number of cabinets that can be deployed in an equipment room
and achievable power density
The floor plan has a great impact on the number of cabinets that can be placed in an equipment room. Generally, the area of an equipment room is divided into 3 m2 per cabinet.
Complexity of power distribution and cooling distribution systems
The floor plan of a data center also has a great impact on the complexity of the power distribution and cooling distribution systems.
01
02
Distribution and predictability of the temperature field in an equipment room
An effective floor plan and the cabinet in-row cooling technology can be used to predict cooling capacity in a simple and reliable manner.
Power consumption of a data center
The floor plan has a great impact on the effect of a cooling system, especially when a traditional cooling system is deployed nearby. The floor plan of specific IT loads can significantly reduce the energy consumption of a data center by affecting the efficiency of the air conditioning system.
04
03
Notes: Why do we need to consider the floor plan in the initial planning phase instead of the detailed design phase? The reasons are as follows:
It is recommended that the data center power density be determined based on the cabinet row. Therefore, the cabinet row layout must be determined before the power density specifications are formulated.
Planning based on the cabinet row or cabinet row group produces the best effect. Therefore, the cabinet row layout must be determined before an effective phase plan is formulated.
The grid of the raised floor and the keel of the suspended ceiling must be aligned with cabinets. Therefore, you must determine the cabinet row layout before positioning the grid and keel.
The criticality and availability of different areas in a data center depend on the actual situation. The cabinet row layout must be determined before a multi-level criticality plan is made.
Achievable power density
The floor plan of a data center has a great impact on the power density that can be achieved. In some cooling architectures, if the floor plan is poor, the allowable power of a specific cabinet will be reduced by more than 50%, which greatly affects the performance of a modern data center. The application of new technologies in modern data centers poses great pressure on the design capability of data centers. In many data centers, users want to build areas with different power densities. The division of these density areas depends on the device layout. Therefore, the floor plan is a key tool for describing and determining the data center density.

## Slide 26: Data Center Floor Plan and Area Division
As recommended by the GB standard, a data center is divided into the following areas in a floor plan: computer room, auxiliary area, support area, and administrative management area.
Gas cylinder room
Office
Air conditioner room
Data center
Medium storeroom
Spare parts warehouse
UPS room
Test and maintenance room
Communications room
Monitoring center
Power transformation and distribution room
Chiller plant
IT R&D labs
Female washroom
Male washroom
Hall
Fire protection and security control room
Air conditioner room
Notes: The division of the data center area determines the application scope and system mode of air conditioners. This section focuses on the layout of air conditioner areas. The typical air conditioner layout is shown in the preceding figure. Air conditioner rooms are deployed on two sides and physically isolated.

## Slide 27: Influence of a Floor Plan on a Cooling System
Affecting the building structure layout of a cooling system
  The equipment room layout of a new or reconstructed data center must be determined, including the positions of walls, doors, windows, supportive columns, observation windows, and major water and electricity connections. If a raised floor is used in the equipment room, the height of the floor and the location of the escalator or elevator at the entrance should also be considered. In addition, other conditions inside the equipment room, such as fresh air, air exhaust in case of faults, and floor drain, also need to be marked and considered.
Affecting the device layout of a cooling system
  The device layout includes the positions for IT, power distribution, and cooling devices. IT device positions can be defined as cabinet positions, without considering specific devices in cabinets. However, the shape of devices such as large enterprise servers is different from that of common cabinets, which have different impact on the structure layout. Therefore, different measures must be taken for such devices. In addition, the characteristics of the airflow path must be considered when IT devices are laid out.
Notes: The measurement value of an equipment room is based on the floor tile. The width of a floor tile is 600 mm or the width of a standard cabinet.
The airflow of common IT cabinets is from the front to the rear. However, the airflow mode of some devices is different, for example, from the front to the top. During device layout, power and cooling devices must be considered. However, many new power and cooling devices can be installed on cabinets or designed to be installed on cabinet rows, which simplifies the layout.

## Slide 28: Floor Plan Example
Identify major issues and set core areas and non-core areas.
  Core areas: areas that need to be focused on during planning, including the core area of a data center, power supply and distribution system, cooling system, and monitoring system.
  Non-core areas: operation center, data center office, unloading platform, and warehouse
Classify equipment rooms and clearly define the power density. Equipment rooms are classified into high-load, medium-load, and low-load equipment rooms based on the deployment and power consumption density of data devices inside. Mark the three types of equipment rooms.
Reduce the impact of the environment on equipment rooms. For a new equipment room, the direction of external walls can be considered. The equipment room can be designed on the east or north side of a building, and passages such as corridors can be reserved on the opposite side.
Design an appropriate area of equipment rooms. An equipment room of a large data center should not be square, but be rectangular. The economic area is 500–800 mm2.
Properly deploy devices.
Fresh air and exhaust air room
Buffer
Storage room
Spare parts room
Hardware maintenance room
Steel cylinder room
Guard room
Central monitoring room
Test room
Network
equipment
room
2# UPS
1# UPS
1# equipment room area
2# equipment room area
Up

## Slide 29: Layout Principles for a Cooling System
The core area should be compactly deployed based on the following considerations:
  Security: Physical deployment in the core area protects the area from risks that may cause damages.
  Easy O&M:
    The cooling system layout should consider the following items in sequence based on the heat transfer direction of servers in the data center: air conditioner indoor unit, water pump room (can be ignored for an air-cooled DX system), and air conditioner outdoor unit platform (chiller platform).
    Power supply for the cooling system: Select an appropriate system based on the equipment room level and reliability requirements to facilitate maintenance and isolation.
  System economy: A compact and reasonable system layout shortens the distribution path of the power distribution and cooling systems, reduces the length of bus cables and pipes, and saves costs.

## Slide 30
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 31: Problems That Can Be Solved by a Modular Architecture Layout
In the traditional data center architecture, determining the layout of all subsystems in a new or existing building is usually a time-consuming process that involves repeated modifications. In this process, the space and location of a large number of devices (including alternative devices) need to be analyzed. Different alternative devices have different requirements on the occupied space, operation, and ports. In the modular architecture, the number of device spaces that need to be considered is reduced significantly. The IT area is used as the core deployment unit, that is, the floor plans of multiple devices are integrated into a single IT area floor plan.
IT area floor plan consisting of the floor plans of multiple devices
Integrated smart module
Smart module with close-coupled cooling
UPS and battery room
IT room
IT room
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Battery
Notes: Several reports recently released by Gartner, a well-known consulting firm, show a trend: The design of the first two generations of data centers cannot meet current and future requirements. New data centers should no longer be a static structure, but a dynamic organism that can evolve with the change of servers and storage infrastructure. Therefore, Gartner recommends that a new data center should adopt flexible, modular, and virtual design.
A controversy about the modular architecture is that it is limited by the system floor plan. If the layout of the IT area or other subsystems is not flexible, the system may fail to fully utilize the available space. Users often need to place data centers in existing spaces of various sizes and shapes. Although there are many examples showing that standardized IT areas cannot make full use of ground space, experience shows that this problem is not serious.

## Slide 32: Planning a Data Center Project Using the Modular Method
Determine the main specifications of the overall design solution, such as the data center, power capacity, future plan, and power density.
Select an existing standard modular architecture that best meets various requirements based on IT specifications.
Determine the special restrictions of the project, such as the existing physical space, power supply, or cooling subsystem.
Determine the modules and other options required to meet the IT specifications based on the restrictions and selected architecture.
Verify that these modules can be deployed under the current project restrictions.
If the selected architecture cannot be used due to restrictions, consider other alternative solutions within the architecture or alternative architectures, or try to adjust restrictions to select the final architecture.

## Slide 33: Floor Plan Comparison
IT room
IT room
IT room
IT room
UPS room
IT room
UPS room
Corridor
IT room
IT room
Corridor
Corridor
Corridor
IT room
IT room
IT room
IT room
Smart
module
room
Smart
module
room
Air conditioner room Air conditioner room
Air conditioner room Air conditioner room
Air conditioner room Air conditioner room
Notes: Compare the two modes when power is the same.

## Slide 34: Huawei Ulanqab Cloud Modular Data Center
To maintain stable growth, make structural adjustments, and improve living standards, Ulanqab seizes the opportunity of coordinated development of the Beijing-Tianjin-Hebei region and rapid growth of the cloud computing industry, and introduces and supports cloud computing and related industries as strategic industries.
In Chahar Economic and Technological Development Area, Huawei has planned an information industry park covering an area of 13 square kilometers to expand the cloud computing service market, provide high-quality cloud computing services for enterprises and institutions in and outside China, and facilitate the rapid development of the cloud computing industry in Ulanqab.
Cloud migration of information application systems of municipal departments is being actively carried out. Currently, 34 service systems have been migrated to the cloud and rolled out.
The mild climate, stable geology, and low energy costs make Ulanqab very suitable for building data centers.
Ulanqab cloud data center

## Slide 35: First-Layer Layout
Diesel generator (DG) area
Route B high-voltage power distribution
Route A high-voltage power distribution
Route B low-voltage power distribution and route B UPS
Route A low-voltage power distribution and route A UPS
Chiller plant
Cooling water pump
Heat storage tank
Chilled water tank
Fire cylinder room
Notes: The data center has two layers. The first layer is the support area, where facilities such as the chillers, fire extinguishing system, and high-voltage power distribution room are deployed.

## Slide 36: Standard Layer Layout
Cooling tower
UPS battery room
Route B low-voltage power distribution and route B UPS
Route A low-voltage power distribution and route A UPS
Low-density data hall module
High-density data hall module
Fire cylinder room

## Slide 37: Modular Data Center
Twelve data halls, six on each layer. The area, shape, and facilities are unified and can be used and expanded by module.
Every two data halls form a group and share a maintenance channel.
The data hall uses the smart module combination, which can be quickly expanded and reserved.
Data hall module
Data hall module
Data hall module
Data hall module
Data hall module
Smart module
Smart module
Smart module
Smart module

## Slide 38: Typical Layout of Cold Aisle In-row Air-Cooled Air Conditioner Indoor Units
Tier III: N active air conditioners + 1 standby air conditioner
Notes: In a typical in-row solution, PDFs are deployed and occupy cabinet positions.

## Slide 39: Power Configurations for Cold Aisle In-row Air-Cooled Air Conditioner Indoor Units
Power supply A comes from power distribution route A, and power supply B comes from power distribution route B (power supplies A and B are turned on at the same time).
Each air conditioner is configured with an ATS/STS.
The ATS/STS can switch power supplies A and B to the indoor and outdoor units.
The power supplies of the indoor and outdoor units should come from the same power supply device and be on the same layer.
Notes: A power failure during the ATS switchover in a Tier III configuration is only an operation event, not a fault.

## Slide 40: Typical Layout of Tier IV Cold Aisle In-row Air-Cooled Air Conditioner Indoor Units
Tier IV: 2N (Half of the indoor units operate to meet the cooling requirements.)
Notes: Tier IV requirements: fault tolerance, partition isolation, continuous cooling, and automatic response
The gas pipe and liquid pipe of an air conditioner are secured on a steel base and can be isolated separately.

## Slide 41: Power Configurations for Tier IV Cold Aisle In-row Air-Cooled Air Conditioner Indoor Units
In a 2N active system, there are N (three) air conditioners in each aisle of the Tier IV system.
Routes A and B are operating at the same time.
Each aisle can bear all cooling loads in the critical environment to meet continuous cooling requirements.
The power supplies of the indoor and outdoor units should come from the same power supply device and be on the same layer.
The air conditioner has a single power supply. The indoor unit can have no ATS/STS.
UPS-A
UPS-B
PDF-A
PDF-B
A/C-A1
A/C-A2
A/C-A3
A/C-B1
A/C-B2
A/C-B3
PDF-B1
PDF-A1

## Slide 42
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 43: Cooling Source Solution Planning for the Cooling System
Classification of cooling source systems
  Any substances with cooling and dehumidification functions can be used as cooling sources for air conditioners on condition that the substances are safe, economical, and environmentally friendly. In general, there are two types of cooling sources for air conditioners: free and manual cooling sources.
  Manual cooling source solutions: DX cooling solution and CW cooling solution; FC source solutions: direct ventilation, rotary wheel heat exchange, and water-based heat exchange
Rotary wheel heat
exchanger FC
FC source
Direct FC
Indirect FC
Water-based FC
FC with direct ventilation
Electrical cooling
(vapor compression)
CW solution
DX solution
Manual
cooling source
Cooling
source

## Slide 44: Data Center Cooling System Solution – DX Air Conditioning System
Water-fluorine side plate heat exchanger
Cooling pipes
Water-cooled condenser
DX indoor unit
DXA
DXW
Easy to install, no need for water system energy-saving construction and maintenance costs
Relatively small and independent cooling cycle, easy to maintain
Applicable to areas with insufficient water sources and places without cooling water systems
Not applicable to large data centers due to lower cooling energy efficiency than that of chillers
The installation distance cannot be too long. Otherwise, the cooling loss is large.
Refrigerant is filled before delivery and does not need to be filled onsite.
Long-distance installation is supported, but waterproof measures should be taken.
Water and glycol are generally required, and the maintenance is complex.
It is applicable to large open-circuit systems with cooling towers or wells.
Air-cooled outdoor unit
DX indoor unit

## Slide 45: Data Center Cooling System Solution – CW Air Conditioning System
CW pump
CW storage tank
Cooling
water pump
CW pump
Cooling
tower
Chiller
Compressor
Water-cooled chiller system
Air-cooled chiller system
Cooling water
outlet
CW outlet
CW return
CW return
CW return
CW return
CW supply
CW supply
CW supply
CW return
CW cooling source
Cooling terminal
Air conditioner control system
Chiller control system
Notes: Water-cooled chiller system:
Consists of the air conditioner, CW pump, water-cooled chiller, cooling water pump, cooling tower, water tank, and other related components.
Air-cooled chiller system:
Consists of the air conditioner, CW pump, air-cooled chiller, water tank, and other related components.

## Slide 46: Air Conditioner Cooling Source Solution – Continuous Cooling
To ensure that the computer room and UPS room that generate much heat can maintain a stable temperature, necessary measures must be taken for the cooling and air conditioning system to provide continuous cooling, so that cooling for systems will not be interrupted due to events such as mains outage and chiller restart.
Class A uninterruptible cooling system with a chilled water tank
According to the white paper on the continuous cooling system for high-density data centers discussed by the Uptime Institute, the cooling system is classified into classes A, B, and C. Class A is the uninterruptible cooling system; class B is the continuous cooling system; class C is the interruptible cooling system. The figure on the left shows the class A uninterruptible cooling system.

## Slide 47
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 48: Data Center Cooling System Solution – FC
FC
Air-based FC
Direct ventilation air handling unit (AHU)
Rotary wheel
Water-based FC
Used together with the chiller
DX FC
Heat exchanger
Used together with the lake and sea water
Fluorine pump
Water-cooled dual-coil pipe
Not applicable area
Applicable area
Advantages:
Directly uses the cooling capacity of the outdoor cooling source, resulting in ultra-low energy consumption.
Makes full use of the seasonal temperature difference of air and water sources.
Has many mature cases in the industry.
Disadvantages:
Indirect FC is complex and prone to single points of failure.
Not applicable to tropical/subtropical areas.
Excessive air conditioning pollution increases IT equipment security risks.

## Slide 49: Data Center Cooling System Solution – Direct Ventilation FC
Mechanical cooling + direct ventilation hybrid cooling
Features:
Multiple control modes, making full use of FC sources and saving energy
Supports underfloor air supply. The indoor air conditioner is basically the same as a common air conditioner.
Supports DX and CW mechanical cooling backup.
The project is complex and has high requirements on the building height and outdoor air quality.
High restrictions on areas, applicable to areas where the annual average temperature is lower than 20°C
Direct ventilation FC
CRAC
20°C
Cold air
Features:
Makes full use of FC sources, improving efficiency and saving energy. The PUE is close to 1.
Easy O&M
No mechanical cooling backup
The project is complex and has high requirements on the building height and outdoor air quality.
Fails to meet the Tier III standards.

## Slide 50: Data Center Cooling System Solution – Other FC Modes
Chillers with FC coil pipes
Indirect air-based FC:
Rotary wheel/heat exchanger
Use natural water sources (such as lake water, groundwater, and seawater) to exchange heat with CW.
DX FC: fluorine pump system
Air-cooled & water-cooled dual-coil pipe system
Notes: Heat exchange between natural water sources and CW: has high requirements on the quality of water sources and has risks of environmental damage.
Air-cooled chiller FC: applied in some scenarios.
Air-cooled & water-cooled dual cooling sources: applied in some scenarios.
Fluorine pump FC: applied in some scenarios.

## Slide 51: Air Conditioner Energy-Saving Solution – Evaporative Cooling Solution
Uses an air-to-air heat exchanger to lower the indoor temperature through the outdoor low-temperature cooling source.
Fully utilizes the difference between dry and wet bulb temperatures to prolong the free cooling time by using the spraying system.
Starts mechanical cooling for auxiliary cooling when the cooling capacity provided by free cooling is insufficient.
Outdoor fresh air
Indoor air return
Indoor
air supply
Outdoor air exhaust
③ Secondary air inlet
T3
T4
Secondary air outlet
Primary air inlet
Water spraying
Primary air outlet
Outdoor air exhaust
Indoor air return
Outdoor fresh air
Outdoor fresh air
Indoor air supply
Indoor air supply

## Slide 52: Key Points for Selecting an Energy-Saving Solution
Data center scale and capacity
  Total cooling load of the cooling source, building footprint, and building floor height
Surrounding environment conditions
  Air temperature and quality, whether there is waste heat and industrial waste heat, whether the power supply is sufficient, and whether there is a renewable cooling source
Building installation environment
  Whether there is a basement, whether there are open spaces outdoors and on the roof, and whether there is a device layer
Performance requirements
  PUE requirements, continuous cooling requirements, reliability level requirements, and control policy complexity
Economy requirements
  If two or more solutions are available, you need to analyze the initial investment and OPEX.

## Slide 53
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 54: Key Points of Indoor Unit Solution Planning
Indoor unit types of in-room, in-row, and in-cabinet cooling
Selection of the airflow organization mode of the indoor unit
Indoor unit layout
Characteristics of underfloor air supply
Optimization scheme of underfloor air supply
Underfloor air supply
Indoor unit type selection and recommendation
Indoor unit type comparison
Layout scenario
Energy-saving mode
Selection of air supply modes
Selection of air return modes

## Slide 55: Indoor Unit Solution – High-Density Data Center In-cabinet Cooling
Chilled water backplane air conditioner
  The indoor unit of the heat exchange system is combined with the cabinet door, and the cooling source is close to the heat source, achieving high cooling efficiency.
  The indoor units of the entire air conditioning system are distributed on the front door of each cabinet and do not occupy extra space of the equipment room. This improves the space utilization of the equipment room.
  Cold aisles are formed inside cabinets and hot aisles are formed outside cabinets. The cooling capacity is concentrated on target devices without loss.
  The heat exchanging capacity of each cabinet is greater than or equal to 10 kW and can be adjusted based on the internal load.
  The cabinet integrates the air conditioner, power supply, and monitoring systems, which are completely modular.
Water refill pipe
The equipment room provides a chilled water pipe. The supply water temperature is 12°C.
Automatic
water refill
valve
Cabinet outlet air temperature: 32°C
Chilled water distribution cabinet
Cabinet temperature controller (AC 220 W)
Outlet air temperature of the front door for cooling: 24°C
Plate heat
exchanger
Rack
Drainpipe
Water return pipe
Return water temperature ≤ 17°C
Anti-leakage
sink

## Slide 56: Indoor Unit Solution – High-Density Data Center In-cabinet Cooling
Water fluorine heat exchanger
Air return
pipe
Gas hose
Backplane
Cabinet
Liquid hose
Liquid
supply pipe
Ground
Chilled water
Cooling architecture of a heat pipe backplane
(gravity-assisted) air conditioner
Energy saving and high efficiency
High-density heat dissipation
No occupation of equipment room space
Flexible configuration and easy installation
Power-based solution improvement
  A refrigerant pump and liquid storage tank are added to the water-cooled refrigerant distribution unit (water fluorine heat exchanger) to meet the strict requirements for the installation position of the water fluorine heat exchanger and solve the problem that no refrigerant is delivered to the remote cabinet.
  The system complexity is increased, the system reliability is reduced, and the cost is greatly increased.
Power heat pipe backplane
Power heat pipe backplane
Water-cooled refrigerant distribution unit
Chilled water return
Chilled water supply
Water-cooled condenser
Solenoid valve
Liquid storage tank
Subcooler
Refrigerant pump
Indoor unit
Main part
Notes: Cooling architecture of a heat pipe backplane (gravity-assisted) air conditioner
  This air conditioner type prevents water from entering the cabinet area and eliminates water leakage risks.
  High plane usage of the computer room (doubtful)
  There are a large number of indoor units (backplanes), pipes, and connectors, and the O&M workload is heavy.
  Refrigerant is delivered by gravity, and there is a risk that the remote cabinet has no available refrigerant.
  Requirements on the installation position and construction of a water fluorine heat exchanger are high.
The hot air exhausted by the server exchanges heat with the backplane installed at the rear of the cabinet. The heat changes the coolant in the backplane from the liquid state to the gas state. The coolant carries heat exhausted by the server to the cooling distribution unit (CDU) at the top of the cabinet. After being cooled by the CDU, the coolant changes to the liquid state and flows back to the backplane by gravity. In this way, a heat exchange cycle is completed. The other side of the CDU is connected to the chilled water circulating system to continuously absorb the heat transferred by the coolant. The chilled water is provided by the outdoor cooling station. Free cooling technologies can also be used based on the site climate.

## Slide 57
Notes: A heat pipe backplane air conditioner has the following features:
  Energy saving and high efficiency: Cooling efficiency is improved by directly cooling the cabinet. The coolant keeps cyclic using the phase change and gravity. No external energy is required for air supply and cooling, which reduces internal energy consumption of the equipment room and is more energy-saving compared with traditional precision air conditioners.
  High-density heat dissipation: The heat dissipation issue of high-density servers is resolved. Currently, the cooling capacity of the heat pipe backplane air conditioner ranges from 8 kW to 16 kW.
  No occupation of equipment room space: The indoor unit is integrated with the cabinet. The issues of insufficient cooling capacity and local overheating in the equipment room are resolved without occupying extra equipment room space.
  Flexible configuration and easy installation: Indoor installation does not affect the normal operation of the server and the server does not need to be shut down. It is applicable to the equipment room reconstruction scenario.
  Other features: Both the indoor unit and CDU are static devices. They are durable and reliable, generate no noise during operating, almost require no maintenance, and provide a comfortable environment for O&M personnel.
The gravity-assisted backplane air conditioner solution has the following problems: 1. The water-cooled condenser is installed higher than the backplane air conditioner. Therefore, there are requirements on the installation clearance and height. 2. Currently, all backplane air conditioners adjust the airflow passively, and have no active flow adjustment device. 3. The existing heat pipe backplane air conditioners mostly use multiple fans. However, if multiple fans are adjusted together, the supply air temperatures will be uneven.

## Slide 58
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 59: Humidity Control Planning in a Data Center
Cabinet
We usually focus on how to reduce the power consumption of the chiller, indoor unit, and water system components of a cooling system. The energy consumption of the humidification system is easily ignored. Using a data center in a northern area as an example, 2% to 3% of the annual energy consumption of the air conditioning system is caused by the humidification system. If the annual energy consumption of the cooling system in a data center is 10 million kWh, 2 to 3 million kWh of energy is consumed by the humidification system in the 10-year life cycle.
The humidity of the waste heat exhaust vent at the rear of an IT device does not need to be measured, and does not affect the availability of the device. It is unrealistic to measure the humidity of each device. For the environment where a cabinet is used, we can only monitor the humidity at the position 1/3 from the cabinet top inside the front door adjacent to the computing device.
Cool air intake temperature: 24°C
Relative humidity: 50%
Dew point temperature: 13°C
Waste heat exhaust temperature: 38°C
Relative humidity: 22%
Dew point temperature: 13°C
Single temperature/humidity measurement point: upper front of the rack near the device
Notes: Every three in-row air conditioners have one backup device to form N+1 redundancy. Generally, one humidifier is deployed for every 12 in-row air conditioners, and one humidifier is associated with one equipment room. The configuration can also be customized. Among every four air conditioners, one air conditioner with the humidification function is configured.

## Slide 60: Humidity Control Policy
Equipment room humidity sensor
Control module for the constant temperature and humidity device
Lower than the
required
humidity
Humidify
Higher than the
required
humidity
Dehumidify
Meet the humidity requirements.
Meet the humidity requirements.
Stop
Stop
Humidification method:
Wet film adiabatic humidification
Dehumidification method:
Condensation dehumidification

## Slide 61: Humidification Mode Selection and Recommendation
Humidifier Type | Wet Film Humidifier | Electrode Humidifier | Infrared Humidifier
Humidification Principle | The water in the sprinkler on the top of the wet film permeates due to gravity and then is absorbed. When dry air passes through the wet film, water molecules absorb heat, evaporate, and turn into moist air. | After AC power is supplied to the electrodes of the storage and steam cylinder in the humidifier, the impurities in water start moving, and kinetic energy is turned into thermal energy. The generated steam is sprayed into the air flow through spray pipes and then evaporates. | Water evaporates when a highlighted infrared quartz lamp is hung above an open water pan. The generated steam spreads to the air flow that requires humidification.
Energy Consumption (Wh/kg) | 15 | 780 | 700
Water Quality Requirement | Clean tap water | Clean tap water or softened water | Clean tap water
Replaced Component | Humidification module (replaced every 8 to 10 years based on the stain status) | Steam cylinder | Infrared lamp
Maintenance Interval | Once per year | Once per year | Once per year
Water Supply Utilization | 30–70% | 75–90% | 75–90%
Advantages | No white powder, self-regulated and clean humidification, no noise, high strength, strong corrosion resistance, anti-microbial, long life cycle, small equipment size, less maintenance, and low OPEX | Key parts made of imported materials, low noise, adjustable humidification amount, high humidification purity, high cost, and often used for equipment room air conditioners | Rapid humidification, no drops and bacteria, excellent control performance, simple deployment, and self-cleaning
Disadvantages | Micro-organism pollution, and temperature decreasing during humidification | High energy consumption and OPEX, prone to scaling and difficult to clean | High energy consumption and OPEX, short life cycle, and high price
Notes: The development trend of humidification systems is the same as that of data centers. Currently, green data centers that are energy-saving and environment-friendly are a major development trend. The development of humidification systems complies with this trend: From the built-in electrode humidifier and infrared humidifier with high energy consumption to the independent wet film humidifier with lower energy consumption, and to the integration of the wet film humidifier into the precision air conditioning system, the humidifier energy consumption has been reduced.
It can be inferred that with the development of humidification technologies, more efficient and energy-saving humidification modes will emerge to meet the requirements of green data centers.

## Slide 62: Fresh Air System Solution
Fresh air solution
Fan section, filtering section, pre-cooling section, humidification section, and heat recovery section
Four solutions
Fan section, filtering section, pre-cooling section, and humidification section
Fan section, filtering section, and heat recovery section
Fan section and filtering section
Solution 1
Solution 2
Solution 3
Solution 4
Modular combination for different scenarios
Solution cost from high to low
Notes: When fresh air is not supplied to the return air vent of the indoor air conditioner (the indoor air conditioner bears the fresh air load), you need to configure a pre-cooling section to meet the supply air temperature requirements. When independent fresh air control is used in humidity control and the outdoor humidity is higher than the indoor control target, you need to configure a dehumidification section (cooling is used for dehumidification generally).
When independent fresh air control is used in humidity control and the outdoor humidity is lower than the indoor control target, you need to configure a humidification section.
To save energy, you can configure a heat recovery section to use exhaust air to preheat or pre-cool the fresh air. There are plate type and rotary-wheel type.
The heating section needs to be configured only when the fresh air unit uses the constant temperature and humidity air supply solution. After cooling and dehumidification, air needs to be reheated and then transferred to the dry bulb working condition for air supply. This is a non-energy saving solution and is not recommended.
In the data center air conditioning field, the fresh air solution is usually combined with free cooling to form an air conditioning system.
Fresh air volume: number of personnel in the equipment room and equipment room space
Outdoor air specifications: outdoor air temperature, humidity, and cleanliness
Economy requirements: If two or more solutions are available, you need to analyze the initial investment and OPEX.

## Slide 63
Implementation of the Data Center Cooling System Planning Process
  System Planning
    Reconstruction
    Floor Plan
    Modular Layout Planning
    Cooling Source Solution Planning
    Energy-Saving Solution Planning
    Indoor Unit Solution Planning
    Humidity Measurement Control and Fresh Air System Planning
    Load Calculation and Indoor Unit Solution Determination

## Slide 64: Calculation of the Cooling Load of Air Conditioners – Determination of the Cooling Load of Air Conditioners
Load calculation
Understand the source of the cooling
load of the air conditioner.
Understand the factors that affect
the cooling load.
Understand temperature requirements
for data centers.
Air conditioner cooling load
Ways to obtain the cooling load when the conditions are not met
Two estimation methods
Estimating the air conditioner cooling load
Understand the purpose of area division.
Calculate the cooling load for each area.
Distinguish the characteristics of air conditioning systems in different areas.
Collecting statistics on air
conditioning functional areas
Select the optimal power density for a data center considering devices.
Select quantity and power of devices in a single cabinet.
Selecting IT power

## Slide 65: Determining the Air Conditioner Indoor Unit Configuration
Determine whether to use in-cabinet, in-row, or in-room cooling based on the power density.
Configure the air conditioner indoor unit capacity based on the estimated service growth rate.
Check whether there are raised floors, whether cold or hot aisle containment exists, whether cold and hot air is mixed, and whether air supply is blocked in different equipment room areas.
Determine PUE requirements, continuous cooling requirements, and reliability level requirements, and evaluate whether hot spots will occur.
If two or more solutions are available, you need to analyze the initial investment and OPEX.
Selection of air
conditioner
indoor units
Calculation of the
number of
indoor units
Indoor unit
layout of the
air conditioning
functional area

## Slide 66
Floor Plan
Modular Layout Planning
Key Points of System Planning

## Slide 67
True or False
For air-side free cooling data center, mountain fire, salt field, and hazardous chemical explosion may affect the running of the cooling system.
Only using direct air free cooling does not meet the Tier III standard.
Notes: 1.T 2.T

## Slide 69
HCIE-DCF-Design
V1.0
Yuewenjun/wx507858
2020/10/7
Lishaofeng/00486775
2020/12/7