## Slide 1: Load Calculation and Air Conditioner Configuration for Data Center Cooling System

## Slide 2
This course consists of two parts:
  Part 1 describes the cooling load calculation principles, related standards, theoretical calculation, and load calculation examples of data center air conditioners.
  Part 2 describes the air conditioners in a data center, in terms of configuration principles and features, recommended model selection, layout selection, and key planning points of the air supply mode.

## Slide 3
On completion of this course, you will be able to:
  Master the load types of data centers.
  Master how to calculate the cooling load of data centers.
  Understand the methods for estimating the cooling load.
  Be able to output simple configuration solutions.
  Get familiar with the types of data center air conditioners.
  Master the type selection of data center air conditioners.
  Master the air conditioner layout and selection in an equipment room.
  Understand the basic air supply modes and selection of data center air conditioners.

## Slide 4
Load Introduction and Calculation for Data Center Cooling System
  Load Types and Control Requirements for Data Center Cooling System
  Cooling Load Calculation and Estimation for Data Centers
  IT Load Calculation and Selection
Air Conditioner Planning and Configuration for Data Center Cooling System

## Slide 5: Air Conditioner Load Types
Air conditioner load types
Cooling load
The amount of cooling (heat taken away by the air conditioning system) that must be provided to the room at a certain moment to maintain the indoor set temperature
Heat load
The amount of heat that must be provided to the room per unit of time to maintain the indoor set temperature
Wet load
The amount of moisture that needs to be removed from (or added to) a room to maintain the indoor relative humidity
Summer
Winter
Phase change
Phase change
Notes: The cooling load consists of sensible heat and latent heat.

## Slide 6: Cooling Load Composition for Air Conditioners in a Data Center
Heat from lighting
Heat from human bodies
Heat from equipment
Convection heat transfer through glass radiation
Unstable heat transfer of the enclosure
Enclosure
Transfer to indoor air
Instantaneous cooling load in the air conditioning area
Radiation
Convection
Latent heat
Main factors:
Outdoor air temperature
and solar radiation heat
Main considerations:
Control requirements for
indoor air temperature
Instantaneous
heat gain
Notes: Instantaneous heat gain refers to the sum of all kinds of heat that enters the room through the enclosure and dissipates inside the room at a certain moment.

## Slide 7: Data Center Temperature Requirements
In China: GB 50174-2017 Code for design of data centers
International: American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) and TIA-942
Focus on the following environmental parameters of the equipment room: temperature, dew point temperature, and relative humidity.
China's standard
US standard
US standard
Notes: The data center design consists of 12 professions, that is, process, planning, building, structure, air conditioning, power, water supply and drainage, power supply and distribution, lighting, communication information, automatic control, and technical economy. The process profession is of utmost priority, and other professions are designed to meet process requirements.
From 2004 to 2011, ASHRAE released three editions of Thermal Guidelines for Data Processing Environments, in which the ambient temperature (intake air temperature) of servers is changed from 20°C–25°C to 18°C–27°C. This initiative has been recognized and supported by electronic information equipment manufacturers in most countries, including China.

## Slide 8: ASHRAE - Suggestions on Temperature and Humidity Design for Data Centers (1)
Recommended and allowable levels for Class 1, Class 2, and NEBS environments
  The following table lists the recommended and allowable levels for Class 1, Class 2, and NEBS environments.
ASHRAE's requirements for Class 1, Class 2, and NEBS environments
Notes: If the equipment is exposed to a high temperature for a long time (the temperature fluctuation frequency or amplitude is large), the equipment fault rate increases, the equipment service life decreases, the hardware/software fault rate increases, and the heat transfer performance decreases. If the temperature exceeds the allowable range for a short time, the equipment is not affected. However, if the equipment runs close to the temperature range for several months, the occurrence probability of the preceding issues increases. Designers and managers should work hard to make the equipment work within the allowable temperature range. ASHRAE (2008) and Telcordia (2001) recommend a temperature range of 18°C to 27°C.
Network Equipment-Building System

## Slide 9: ASHRAE - Suggestions on Temperature and Humidity Design for Data Centers (2)
Illustration of allowable Class 1 environmental requirements on the psychrometric chart
  The psychrometric chart shows the recommended temperature and humidity ranges and the allowable maximum ranges for Class 1 environments.

## Slide 10: Comparison of Environment Requirements Inside Data Centers
The operating conditions of electronic information equipment manufactured by some manufacturers in and outside China are as follows:
  Dell: 10–35°C, 20–80%; HP: 10–35°C, 20–80%
  Huawei: 10–35°C, 8–85%; Lenovo: 10–35°C, 8–80%
Item | GB 50174 | ASHRAE
Temperature (°C) | 18–27°C | 18–27°C
Humidity | The relative humidity is less than or equal to 60%. | 20–80%
Temperature change rate | < 5°C/h if a magnetic tape drive is used < 20°C/h if a magnetic tape drive is used | The recommended maximum inlet temperature change for Classes 1 and 2 is 5 K/h.
Dew point temperature (°C) | 5.5–15°C | 17–21°C recommended for Classes 1 and 2
Cleanliness | < 17,600,000 particles | Calculation based on the filtering level
Notes: Particle in GB 50174: number of suspended particles with a diameter greater than or equal to 0.5 µm in 1 m3 air
The ASHRAE (2008) recommended maximum inlet temperature change is 5 K/h for Classes 1 and 2. The typical requirements for tapes are that the change rate is less than 2 K/h and the relative humidity change is less than 5%/h (ASHRAE, 2004).
The dew point temperature is used instead of relative humidity to make the measurement more accurate. Both the dew point temperature and relative humidity can indicate the moisture content in air. When the moisture content in air remains unchanged, the dew point temperature is a fixed value, while the relative humidity varies with the temperature. Therefore, GB 50174-2017 uses dew point temperature to indicate the moisture content in air.

## Slide 11: How to Determine the Temperature and Humidity of Data Centers
The specific temperature and humidity range must comply with the customer's requirements. If there is no specific requirement, you are advised to select based on the following principles:
  If there is an aisle containment, the recommended temperature for the cold aisle or server inlet is 23°C±2°C or 24°C±2°C.
  If there is no aisle containment, the recommended server inlet temperature is 23°C±2°C or 24°C±2°C. Relative humidity: 50%±5%
Cold aisle containment
Hot aisle containment
Notes: The preceding lists the temperature control recommendations for Huawei modular data centers, which are based on the China's standards. The content about dew point temperature in the China's standards is for reference only.

## Slide 12
Load Introduction and Calculation for Data Center Cooling System
  Load Types and Control Requirements for Data Center Cooling System
  Cooling Load Calculation and Estimation for Data Centers
  IT Load Calculation and Selection
Air Conditioner Planning and Configuration for Data Center Cooling System

## Slide 13: Cooling Load to be Calculated for Data Centers
The cooling load of air conditioners consists of the total heat generated by all components in the data center and the heat sources from the surrounding environment.
Heat from equipment in data centers
Heat from IT equipment, uninterruptible power supply (UPS), battery room, as well as power transformation and distribution equipment
Heat transferred through the enclosure
The enclosure refers to the walls, doors, and windows around the building space, which can effectively resist the impact of adverse environment.
Heat from human bodies and lighting
Activity areas and lighting facilities that are always on
Pipes deployed in places where people work, and so on
Heat generated by the fresh air system
Heat generated due to the working of the fresh air system or heat leaked through gaps
Fresh air unit, window, gap, and so on
Communications equipment
UPS, power distribution unit (PDU), battery, and cable
Focus on the heat that enters the room through heat conduction and partial heat storage.
Proportion: 80%
Proportion: 5%–20%
Notes: For large data centers with outdoor walls and roofs, outdoor heat enters the data center through walls and roofs in the form of heat conduction and radiation. The air conditioning system must take away the heat. The cooling load of the air conditioning system must include this part of heat.

## Slide 14: Data Center Cooling Load Calculation - IT Equipment and UPS
Heat from IT equipment
Definition
Heat from IT equipment
Calculation
Heat from IT equipment: QIT = N x p x η1
Description
N: planned rack quantity
p: power density of a single rack
η1: simultaneous full-load coefficient (determined based on customer requirements)
Generally, there is no special requirement and the default value is 1.
Definition
The UPS also generates heat. Generally, the UPS has heat dissipation equipment such as fans. Its heat is related to its actual power and power factor.
Calculation
It can be calculated as follows: QUPS = N (1 – η)
Description
Q: heat dissipation capacity (kW)
N: actual power consumption (kW)
η: efficiency. The value ranges from 0.96 to 0.97.
UPS heat dissipation calculation
Notes: The heat from IT equipment is generally a stable value.
IT equipment includes communication equipment, servers, storage equipment, and switches.

## Slide 15: Data Center Cooling Load Calculation - Heat from Power Transformation and Distribution Equipment
Heat generated by power distribution equipment, such as PDUs, in Internet data centers (IDCs):
Definition
Heat from PDUs and low-voltage (LV) power distribution equipment
Calculation
Heat from PDUs
When the PDU is not equipped with an isolation transformer, the amount of heat generated is 0.5% x IT power consumption (kW).
When the PDU is equipped with a built-in isolation transformer, the amount of heat generated is 2% x IT power consumption (kW).
Heat from LV power distribution equipment
Heat from LV power distribution equipment = Total active power of the system (kW) x (1 – 99.5%)
Heat from LV power distribution equipment = Total apparent power of the system (kVA) x Power factor x Load rate x (1 – 99.5%)

## Slide 16: Data Center Cooling Load Calculation – Heat from Equipment in the Battery Room
Heat from the battery room
Definition
Heat generated by batteries during charging
Calculation
If no value is provided, use the following formula to calculate: QBAT = q x U/2 x C x N
Description
q: heat dissipation (W) per Ah at the voltage of 2 V. When the battery charging current is 0.1C, 0.15C, 0.2C and 0.3C, the value is 0.01, 0.015, 0.02, and 0.03 respectively.
U: battery voltage (V)
C: battery capacity (Ah)
N: total number of batteries
Notes: Generally, a large-capacity UPS is deployed in an independent room. It has certain requirements for the temperature, humidity, and cleanliness of the indoor environment.

## Slide 17: Data Center Cooling Load Calculation – Other Heat Sources
Item | Definition | Calculation | Remarks
Heat from the enclosure | Heat transferred to the data center through walls, doors, and windows due to temperature difference | Calculated based on stable heat transfer: Qw =K x F x (t1 – t2) K: heat transfer coefficient, which is calculated based on the building or ranges from 1.4 to 1.6. A value of t1 minus t2 may be determined based on 8°C to 10°C. | If there is no detailed calculation condition, estimate the heat dissipation by each unit: Q = A x n x 0.02 (kW/m2). In the formula, A indicates the area of the equipment room (m2), and n indicates the number of external walls, floors, and roofs that are adjacent to a non-air-conditioning room. (If the four walls of the equipment room, floor, and roof are adjacent to the non-air-conditioning room, the value of n is 6. If none of them is adjacent to the non-air-conditioning room, the value of n is 0.)
Heat from human bodies | Cooling load caused by human body heat dissipation | Human body sensible heat cooling load: Qr = p x N | p = 0.18 kW (sensible heat and latent heat generated by human bodies in the equipment room at a temperature of 24°C) N: maximum number of persons that may appear in the equipment room at the same time in normal cases.
Heat from lighting | Cooling load generated by the lighting system deployed in a room | Heat generated by lighting: Q = 1.2 x P x η1 x (Xt – T) | P: installation power of lighting equipment in the equipment room (kW) η1: simultaneous usage coefficient (provided by the electrical profession) Xt – T: cooling load coefficient of lights from the calculation time t to the light-on time T (obtained from the design manual). 1.2 is the heat dissipation coefficient additionally added for the fluorescent lamp rectifier. If there is no detailed calculation condition, estimate the heat dissipation by each unit: 15 W/m2 for the IDC and UPS equipment room, and 10 W/m2 for the battery room and LV power distribution room.
Heat from the fresh air system | Heat generated by the fresh air system | Qx = M x (h1 – h2) | M: fresh air volume in the equipment room (kg/s); h1: outdoor air enthalpy (kJ/kg); h2: indoor air enthalpy (kJ/kg) If the fresh air load is carried by the chilled water system of the data center, it should be included in the total cooling load. If the fresh air load is carried by an independent direct expansion (DX) air conditioner, it is not included in the total cooling load.

## Slide 18: Load Calculation by Region (1)
Table for air conditioner cooling load calculation by region
Region |  |  | 
Equipment Room | Floor | Area (m2) | Net Height (m)
IDC 1 |  |  | 
Heat from Equipment in the Data Hall |  |  |  |  |  |  | 
Number of Cabinets (N) | Average Cabinet Power (kW/Rack) | Load Coefficient η1 | Simultaneous Full-Load Coefficient η2 | Heat from IT Equipment (kW) | Heat Dissipation Load Coefficient of the PDU | Heat Dissipation Load of the PDU (kW) | Total Equipment Load (kW)
Personnel Heat Dissipation |  | 
Heat Dissipation Per Unit (W/Person) | Number of Personnel | Total Personnel Heat Load (kW)
Heat from Lighting | 
Heat Dissipation Per Unit (W/m2) | Total Lighting Load (kW)
Heat from the Enclosure |  |  |  |  |  |  |  | 
Heat Transfer Coefficient of the External Wall K1 W/(m2∙°C) | Total External Wall Area (m2) | Rooftop Heat Transfer Coefficient K2 W/(m2∙°C) | Total Rooftop Area (m2) | Indoor Design Temperature (°C) | Highest Outdoor Temperature | Heat Transfer Load of the External Wall (kW) | Heat Transfer Load of the Rooftop (kW) | Total Structure Load (kW)
Total Room Cooling Load | 
Total Cooling Load (kW) | Area Load (kW/m2)

## Slide 19: Load Calculation by Region (2)
Load summary table
Equipment Room | Heat Dissipation Load of Equipment (kW) | Heat Dissipation Load of Personnel (kW) | Heat Dissipation Load of Lightings (kW) | Heat Dissipation Load of the Enclosure (kW) | Total Room Cooling Load (kW) | Redundancy Coefficient of Room Air Conditioners | Total Cooling Capacity of Room Air Conditioners (kW)
IDC 1 |  |  |  |  |  |  | 
IDC 2 |  |  |  |  |  |  | 
UPS room 1 |  |  |  |  |  |  | 
UPS room 2 |  |  |  |  |  |  | 
Battery room |  |  |  |  |  |  | 
LV power distribution room 1 |  |  |  |  |  |  | 
LV power distribution room 2 |  |  |  |  |  |  | 
Operation room |  |  |  |  |  |  | 
... |  |  |  |  |  |  | 
Total Cooling Load (kW) |  |  |  |  |  |  | 
Notes: Note: If the load of the fresh air unit is carried by the chiller, the fresh air load should be included in the cooling capacity calculation of the chiller. Otherwise, it is not included.

## Slide 20: Data Center Cooling Load Estimation Overview
Two estimation methods:
  Calculation by unit area
    It is rough estimation based on the actual accumulated air conditioner load estimation counters. The air conditioner load counter refers to the cooling capacity required by the equipment in every 1 m2 air conditioning area of the building.
  Load statistics method (modular solution)
    Modular solution: it is estimation based on the number of cabinets and power density of a single cabinet. Number of cabinets x Power density x Simultaneous coefficient (0.6–0.8 or 1) x Comprehensive coefficient (1.3–1.5 for open aisles and 1.1–1.2 for aisle containment)
Notes: The total net cooling capacity of the air conditioners (after the heat generated by the air conditioners is reduced) should be greater than the cooling load of the air conditioners. The redundancy coefficient is usually multiplied by 1.05 to 1.1.

## Slide 21: Data Center Cooling Load Estimation – Calculation by Unit Area
In the actual engineering solution design, due to the complexity of the building structure, select the cooling capacity required by the equipment room unit area according to the following table, and then calculate the cooling capacity requirement according to the total area.
For example, the heat dissipation capacity of a 130 m2 computer room is calculated based on 350 W/m2: 130 x 0.35 = 45.5 kW.
Equipment Room Type | Power Density
Telecom switch room and mobile base station | 350–500 W/m2
Transmission equipment room | 250–350 W/m2
IDC | 600–800 W/m2
Computer room and control center | 350–500 W/m2
Precision machining workshop | 300–350 W/m2
Standard test room and calibration center | 250–300 W/m2
UPS, battery room, and power equipment room | 300–350 W/m2
Area Method
The estimated load of an equipment room is determined based on the empirical statistics of equipment rooms of the same type. When this method is used, the actual power value and source must be specified. However, the load density changes greatly due to the development of the power trend. Therefore, the estimated value can only be used as a reference.
Notes: This method is not used for modular data centers.

## Slide 22: Data Center Cooling Load Estimation – Load Statistics Method (Modular Solution)
Equipment Room | Number of Racks | Power Density of a Single Rack (kW) | UPS Power (kW) | Battery Cabinet Power (Optional) | Simultaneity Coefficient (Recommended) | Comprehensive Coefficient (Aisle Containment or Open Aisle) | Total Cooling Capacity (kW)
IDC 1 |  |  |  |  |  |  | 
IDC 2 |  |  |  |  |  |  | 
... |  |  |  |  |  |  | 
Total Cooling Load (kW) |  |  |  |  |  |  | 

## Slide 23
Load Introduction and Calculation for Data Center Cooling System
  Load Types and Control Requirements for Data Center Cooling System
  Cooling Load Calculation and Estimation for Data Centers
  IT Load Calculation and Selection
Air Conditioner Planning and Configuration for Data Center Cooling System

## Slide 24: Discussion
The key to cooling load calculation is to obtain the heat dissipation capacity of IT equipment. However, in some cases, the available computing capability is calculated based on the equipment quantity that can be satisfied by the planned construction area, or the required area is calculated based on the equipment quantity. So, what is the relationship between the data center area and the equipment quantity? How can we calculate the equipment quantity based on the data center area?
&
&
Equipment room layout
Number of cabinets
Equipment quantity
Notes: It is common that the available computing capability is calculated based on the equipment quantity that can be satisfied by the planned construction area, or the required area is calculated based on the equipment quantity.

## Slide 25: Mapping Between the Data Center Area and the Equipment Quantity
The composition of a data center should be determined based on system features and equipment requirements. It is recommended that the data center be composed of functional areas such as the computer room, auxiliary area, support area, and administrative area.
When the area is determined, due to the main technology development, as well as positioning and composition of the data center, the following factors affect the calculation of the number of cabinets:
Data center construction level
Different scenarios
Different technologies
Other factors
Notes: (1) Data center construction level: According to different definitions of data center levels in and outside China, data centers of different levels have strict requirements on availability and annual shutdown time. Details are not described herein. However, data centers of different levels have different requirements on power supply and distribution and heating, ventilation and air conditioning (HVAC). As a result, the auxiliary construction area varies greatly.
For example, Class A data centers require 2N power supply systems, and air conditioners dedicated for the equipment room work in N+X redundancy mode. Class B data centers require N+1 power supply systems, and air conditioners dedicated for the equipment room work in N+1 redundancy mode.
(2) Impact of different scenarios on data center composition: Some data centers are constructed using idle factories and warehouses. From the perspective of reasonable space utilization, these data centers are different from new data centers. In addition, the building structure and shape of the building may have some individual differences on the effective usage of the data center area.
(3) Impact of different technologies on data center composition: From the perspective of air conditioning, the selection of air-cooled and water-cooled technologies affects not only the air supply mode and airflow organization design of the data center, but also the space of the auxiliary area. For example, the water-cooled condensation tower is generally deployed on the top of the data center building, while the air-cooled air conditioners are distributed by floor.
(4) Other factors: The importance of services involved in some data centers or the wide application of professions will increase the number of maintenance personnel. Whether the space occupied by the maintenance personnel is included in the overall area and whether the data center display area is included in the overall planning affect the calculation process of the two factors.

## Slide 26: Mapping Between the Data Center Area and the Equipment Quantity
Based on the preceding factors, assume that a new Class A data center covers an area of about 10,000 square meters and has about 100 maintenance personnel. In this scenario, the number of cabinets is calculated as follows:
Class A data center
10000 m2
100
?

## Slide 27: Mapping Between the Data Center Area and the Equipment Quantity
Calculation rule
  A1 = S x N, where A1 is the area of the computer room, S is the occupied area of a single cabinet (3 m2/PCS based on the project positioning), and N is the number of all cabinets in the computer room.
  A2 is the total area of the auxiliary area and support area. It is 2.5 times the area of the computer room A1.
  A3 is the area of the administrative area, which is 5 m2/person.
A = A1 + A2 + A3
If A = 10000 = A1 + A2 + A3 = A1 + 2.5A1 + 500, A1 = 2714, N = 905
The number of IT cabinets is about 815.
A1
A1
A2
A2
A3
Notes: Based on the modular design of the data center, assume that every 20 cabinets form one module, including 18 IT cabinets and two power supply and distribution cabinets. The number of IT cabinets accounts for about 90% of the total number of cabinets in the computer room.

## Slide 28: Selection of the Optimal Power Density for Data Centers from the Perspective of Equipment
With the development of IT technologies, density planning (and overall capacity planning) is undoubtedly a challenge for IT management personnel. The technology update period is usually two to four years, and it is difficult to determine the required type and power consumption of IT equipment in the future. Therefore, enterprises tend to overestimate future requirements and reserve safety margins.
Typical power density of different types of cabinets
Typical data center cabinet types
Hot spot due to uneven deployment
Notes: With the development of IT technologies, density planning (and overall capacity planning) is undoubtedly a challenge for IT management personnel. The technology update period is usually two to four years, and it is difficult to determine the required type and power consumption of IT equipment in the future. Therefore, enterprises tend to overestimate future requirements and reserve safety margins. It is important to understand the following IT equipment attributes:
  The nameplate does not reflect the actual power consumption.
  The power consumption of IT equipment is not constant.
  The performance (computing) per watt is improving.
The equipment cannot reach the rated power on the nameplate. Generally, the power of IT equipment does not exceed 50% of the rated value on the nameplate. The actual power depends on the equipment configuration.

## Slide 29: Quantity and Power of Equipment in a Single Cabinet
U space of a cabinet
Switch | PDU| Heat dissipation and others
U space arrangement
  In a data center, a 42 U cabinet, excluding the space occupied by switches and PDUs, provides a total of 36 U space. Considering that 1 U space is reserved between adjacent equipment in a cabinet for heat dissipation, each cabinet can house a maximum of eighteen PCS of 1 U equipment or twelve PCS of 2 U equipment.
Power adaptation analysis
  5 kW+: The power density of most single cabinets in a data center is lower than 5 kW. However, with the popularity of supercomputing and other services in recent years, high-density or ultra-high-density cabinets are gradually available in the market.
  According to the statistics in 2019, the average power consumption of a single cabinet is 5 kW, 8 kW, and 10 kW, and the service proportion is 50%, 30%, and 20%, respectively.
  It is recommended that the average power consumption of a single cabinet be about 7 kW.
  5 kW cabinets are also widely used in data centers.

## Slide 30
Load Introduction and Calculation for Data Center Cooling System
Air Conditioner Planning and Configuration for Data Center Cooling System
  Air Conditioner Configuration Principles and Selection of Data Center Cooling System
  Air Conditioner Planning and Configuration for Data Center Cooling System
  Air Supply Mode and Selection of Data Center Cooling System

## Slide 31: Comparison of Air Conditioner Configuration Principles for Data Center Cooling System
Comparison of Uptime, GB 50174, and TIA-942
Uptime | GB 50174 | TIA-942 | Functional Requirements | Equipment Configuration | System Configuration
Tier I | Class C | I | Basic requirement, no redundancy | N | The system meets basic requirements and has no redundancy.
Tier II | Class B | II | Redundant component | N+X (X = 1 to N) | N+1 redundancy provides an additional device, module, path, or system beyond the basic requirements. Failure or maintenance of any individual device, module, or path will not affect normal operation.
Tier III | Class A | III | Two systems are maintained concurrently. | 2N or 2 (N+1) | Two systems are deployed in active/standby mode. 2N redundancy provides each of the basic systems with two completely same devices, modules, paths, or systems. Entire failure or maintenance of a system, including device, module, path, and system, will not affect normal operation.
Tier IV |  | IV | Fault tolerance | 2N or 2 (N+1) | Two systems run concurrently.
Notes: Tier I: small- and medium-sized users whose services can be interrupted
Tier II: ultra-high-speed, ultra-large-capacity engineering and supercomputing centers
Tier III: data centers or equipment rooms that: mainly performs distributed data processing and sharing operations for massive storage and high-speed information query; and can tolerate occasional or transient service interruption and maximize profits. Typical application industries include BAT, telecom, and hosting enterprises.
Tier IV: data centers or equipment rooms that perform secure, precise, short-delay, and continuous data processing and sharing. The tolerance of service interruption is zero. Typical application industries include finance, civil aviation, petrochemical, and military.

## Slide 32: Air Conditioner Forms of In-Room, In-Row, and In-Cabinet Cooling
The air conditioning system in a data center has two important functions: providing the total cooling capacity and distributing cold air to IT loads.
For in-room, in-row, and in-cabinet cooling air conditioners, how to distribute cold air to loads is the key. The airflow organization is limited by the equipment room structure and layout. The actual airflow is invisible during the implementation and varies greatly with the deployment location.
Air conditioner forms of in-room, in-row, and in-cabinet cooling

## Slide 33: Comparison Among In-Room, In-Row, and In-Cabinet Solutions in Flexibility
Type |  | In-Room | In-Row | In-Cabinet
Flexibility | Advantages | When the power density is less than 4 kW/rack, the cooling mode can be quickly changed. | Easy to plan for any power density Easy to share cooling capacity | Easy to regulate any power density; separated from the existing cooling system
 | Disadvantages | The efficiency is low when the airflow is not contained in the entire environment. | The cold and hot aisle layout is required. | The cooling capacity cannot be shared with other cabinets.
Flexibility
Conclusion: In-cabinet cooling is the most flexible mode, can be deployed in shortest time, and supports the highest power density. However, extra expenditure is required.
√

## Slide 34: Comparison Among In-Room, In-Row, and In-Cabinet Solutions in System Availability
Type |  | In-Room | In-Row | In-Cabinet
System availability | Advantages | Redundant devices can be shared among all cabinets in a data center. | Redundant devices can be shared among multiple cabinets in an area. Cooling close to heat sources eliminates the vertical temperature gradient. | Cooling close to heat sources eliminates hot spots and vertical temperature gradient. High fault tolerance
 | Disadvantages | Airflow containment is required to isolate cold air from hot air. | Redundancy must be deployed in each cabinet area. | Redundancy must be considered for each cabinet.
System availability
Conclusion: Both the in-row and in-room cooling has high system availability and good sharing.
√
√

## Slide 35: Comparison Among In-Room, In-Row, and In-Cabinet Solutions in Life Cycle Cost
Type |  | In-Room | In-Row | In-Cabinet
Initial investment cost | Advantages | The floor can be configured, and the airflow organization mode can be changed easily. | The cooling requirements can be met, and the planning and engineering workload is eliminated or reduced. | Prefabricated systems and standardized components eliminate or reduce the planning and engineering workload.
 | Disadvantages | The air supply is too heavy. The pressure in the underfloor downflow area depends on the equipment room size and floor depth. | The initial cost increases as the data center scale increases. | Due to the change of power, the cooling system is over-planned, which wastes the cooling capacity and increases the initial cost.
Initial investment cost
Conclusion: In in-room underfloor downflow cooling solutions, the cooling distribution mode can be quickly changed by reconfiguring the perforated floor. In a low-density data center, all cabinets share cooling redundancy. This mode is cost-effective and simple.
√

## Slide 36: Comparison Among In-Room, In-Row, and In-Cabinet Solutions in Maintainability
Type |  | In-Room | In-Row | In-Cabinet
Maintainability | Advantages | The cooling equipment is located around or outdoors to keep technical personnel away from IT equipment. | Modular components shorten the shutdown time. Standardized components reduce the need for technical personnel. | Standardized components reduce the need for technical personnel. Internal personnel can complete routine maintenance.
 | Disadvantages | The system is large and needs to be maintained by trained technical personnel or experts. | The cooling equipment is located in the cabinet row. Therefore, technical personnel need to be close to IT equipment to maintain the cooling equipment, which increases risks. | 2N redundancy is required for concurrent maintenance.
Maintainability
√
√
Conclusion: The in-cabinet and in-row cooling have higher maintainability. Modular components greatly reduce the maintenance difficulty.

## Slide 37: Summary
Conclusion: The in-room and in-row airflow containment design provides excellent flexibility, predictability, and scalability, reduces energy consumption and TCO, and improves availability, meeting the requirements of data centers. In-cabinet cooling applies to high-density and high-precision deployment or unstructured layout. In-room cooling without airflow containment will still be an effective solution for low-density data centers.
In-room air conditioner + aisle containment solution
In-row air conditioner + aisle containment solution

## Slide 38
Load Introduction and Calculation for Data Center Cooling System
Air Conditioner Planning and Configuration for Data Center Cooling System
  Air Conditioner Configuration Principles and Selection of Data Center Cooling System
  Air Conditioner Planning and Configuration for Data Center Cooling System
  Air Supply Mode and Selection of Data Center Cooling System

## Slide 39: Data Center Air Conditioner Layout
Three common data center layouts: in-room air conditioner + open aisle, in-room air conditioner + aisle containment, and in-row air conditioner + aisle containment
Equipment room layout for the water-cooled solution
In-room air conditioner + open aisle
In-room air conditioner + aisle containment
In-row air conditioner + aisle containment
1
2
3
Equipment room layout for the air-cooled solution
In-room air conditioner + open aisle
In-room air conditioner + aisle containment
In-row air conditioner + aisle containment
4
5
6
Notes: Describe three common data center layout solutions (in-room air conditioner + open aisle, in-room air conditioner + aisle containment, and in-row air conditioner + aisle containment), and compare them in terms of equipment room utilization, supported power density, energy saving, and safety.

## Slide 40: Water-Cooled Solution: In-Room Air Conditioner + Open Aisle
Equipment room area: 188 m2
Number of racks: 56
Power density: 4 kW/rack
Estimated cooling load of the equipment room: Number of racks x Power density x Simultaneous coefficient (0.6 to 0.8) x Comprehensive coefficient (open aisle: 1.3 to 1.5; aisle containment: 1.1 to 1.2) = 56 x 4 x 0.8 x 1.4 = 250 kW
Air conditioner configuration: four 100 kW air conditioners (three active and one standby)
Typical PUE: 2.0–3.5
Summary: It is a traditional solution, adopting air supply mode using air caps, and in-room air conditioner + open aisle. The cooling effect is poor due to mixing of cold and hot air. Long-distance air supply is prone to hot spots. Generally, the density of single cabinet does not exceed 4 kW/rack. It has high PUE and energy consumption. The equipment room utilization rate and safety is average. One standby air conditioner is available.
1
In-room air conditioner + open aisle PUE: 2.0–3.5

## Slide 41: Water-Cooled Solution: In-Room Air Conditioner + Aisle Containment
Equipment room area: 188 m2
Number of racks: 56
Power density: 4 kW/rack
Estimated cooling load of the equipment room: Number of racks x Power density x Simultaneous coefficient (0.6 to 0.8) x Comprehensive coefficient (open aisle: 1.3 to 1.5; aisle containment: 1.1 to 1.2) = 56 x 4 x 0.8 x 1.15 = 206 kW
Air conditioner configuration: three 100 kW air conditioners (two active and one standby)
Typical PUE: 1.75–1.9
Summary: It is an optimized traditional solution, adopting underfloor downflow, and in-room air conditioner + aisle containment. The cooling effect is good because the cold and hot air is separated. Long-distance air supply is prone to hot spots. Generally, the density of single cabinet does not exceed 5 kW/rack. Moderate PUE and energy consumption. The equipment room utilization rate and safety is average. One standby air conditioner is available.
In-room air conditioner + aisle containment PUE: 1.75–1.9
2
Notes: The estimated cooling load of the equipment room is 206 kW. During configuration, a 200 kW load is configured. The error of this part has been considered in the comprehensive coefficient of 1.15.

## Slide 42: Water-Cooled Solution: In-Row Air Conditioner + Aisle Containment
Equipment room area: 188 m2
Number of racks: 60
Power density: 4 kW/rack
Estimated cooling load of the equipment room: Number of racks x Power density x Simultaneous coefficient (0.6 to 0.8) x Comprehensive coefficient (open aisle: 1.3 to 1.5; aisle containment: 1.1 to 1.2) = 60 x 4 x 0.8 x 1.15 = 220 kW. The estimated cooling load of each module is 110 kW.
Air conditioner configuration: six 30 kW air conditioners in each module (four active and two standby)
Typical PUE: 1.45–1.65
Summary: It is a modular solution. The cooling effect is good because the cold and hot air is separated. Short-distance precise air supply eliminates hot spots. High-density deployment is adopted. Generally, the density of single cabinet does not exceed 13 kW/rack. Low PUE and energy consumption. The equipment room utilization rate is high, and more cabinets can be deployed compared with the traditional solution. Higher safety. Two standby air conditioners are available.
In-row air conditioner + aisle containment PUE: 1.45–1.65
3
Notes: The number of racks varies according to the installation distance of the air conditioners and the air supply distance. The in-room solution and in-row solution have their own requirements on the number of racks.

## Slide 43: Air-Cooled Solution: In-Room Air Conditioner + Open Aisle
Equipment room area: 188 m2
Number of racks: 64
Power density: 4 kW/rack
Estimated cooling load of the equipment room: Number of racks x Power density x Simultaneous coefficient (0.6 to 0.8) x Comprehensive coefficient (open aisle: 1.3 to 1.5; aisle containment: 1.1 to 1.2) = 64 x 4 x 0.8 x 1.4 = 286 kW
Air conditioner configuration: four 100 kW air conditioners (three active and one standby)
Typical PUE: 2.5–3.5
Summary: It is a traditional solution, adopting air supply mode using air caps, and in-room air conditioner + open aisle. The cooling effect is poor due to mixing of cold and hot air. Long-distance air supply is prone to hot spots. Generally, the density of single cabinet does not exceed 4 kW/rack. It has high PUE and energy consumption. The equipment room utilization rate is average. Moderate safety. One standby air conditioner is available.
In-room air conditioner + open aisle PUE: 2.5–3.5
4
Notes: Due to different installation distance requirements, the air-cooled solution has multiple cabinets compared with the water-cooled solution.

## Slide 44: Air-Cooled Solution: In-Room Air Conditioner + Aisle Containment
Equipment room area: 188 m2
Number of racks: 64
Power density: 4 kW/rack
Estimated cooling load of the equipment room: Number of racks x Power density x Simultaneous coefficient (0.6 to 0.8) x Comprehensive coefficient (open aisle: 1.3 to 1.5; aisle containment: 1.1 to 1.2) = 64 x 4 x 0.8 x 1.15 = 236 kW
Air conditioner configuration: four 100 kW air conditioners (three active and one standby)
Typical PUE: 1.9–2.0
Summary: It is an optimized traditional solution, adopting underfloor downflow, and in-room air conditioner + aisle containment. The cooling effect is good because the cold and hot air is separated. Long-distance air supply is prone to hot spots. Generally, the density of single cabinet does not exceed 5 kW/rack. Moderate PUE and energy consumption. The equipment room utilization rate is average. Moderate safety. One standby air conditioner is available.
In-room air conditioner + aisle containment PUE: 1.9–2.0
5

## Slide 45: Air-Cooled Solution: In-Row Air Conditioner + Aisle Containment
Equipment room area: 188 m2
Number of racks: 68
Power density: 4 kW/rack
Estimated cooling load of the equipment room: Number of racks x Power density x Simultaneous coefficient (0.6 to 0.8) x Comprehensive coefficient (open aisle: 1.3 to 1.5; aisle containment: 1.1 to 1.2) = 68 x 4 x 0.8 x 1.15 = 250 kW. The estimated cooling load of each module is 125 kW.
Air conditioner configuration: six 35 kW air conditioners in each module (four active and two standby)
Typical PUE: 1.5–1.7
Summary: It is a modular solution. The cooling effect is good because the cold and hot air is separated. Short-distance precise air supply eliminates hot spots. High-density deployment is supported. Generally, the density of single cabinet does not exceed 13 kW/rack. Low PUE and energy consumption. The equipment room utilization rate is high, and more cabinets can be deployed compared with the traditional solution. Higher safety. Two standby air conditioners are available.
In-row air conditioner + aisle containment PUE: 1.5–1.7
6

## Slide 46: Comparison Between Three Solutions
Item |  | Solution 1: In-Room + Open Aisle | Solution 2: In-Room + Aisle Containment | Solution 3: In-Row + Aisle Containment | Conclusion
Equipment room area |  | 188 m2 | 188 m2 | 188 m2 | -
Water-cooled solution | Equipment room utilization rate | 56 racks | 56 racks | 60 racks | Solution 3 has higher equipment room utilization rate.
 | Maximum power density | 4 kW/rack | 5 kW/rack | 13 kW/rack | Solution 3 supports higher power density.
 | PUE | 2.0–3.5 | 1.75–1.9 | 1.45–1.65 | Solution 3 has lowest PUE and is most energy-saving.
 | Safety | Three active air conditioners and one standby air conditioner in the equipment room | Two active air conditioners and one standby air conditioner in the equipment room | Four active air conditioners and two standby air conditioners in the module | Solution 3 has more standby air conditioners and features higher safety.
Air-cooled solution | Equipment room utilization rate | 64 racks | 64 racks | 68 racks | Solution 3 has higher equipment room utilization rate.
 | Maximum power density | 4 kW/rack | 5 kW/rack | 13 kW/rack | Solution 3 supports higher power density.
 | PUE | 2.5–3.5 | 1.9–2.0 | 1.5–1.7 | Solution 3 has lowest PUE and is most energy-saving.
 | Safety | Three active air conditioners and one standby air conditioner in the equipment room | Three active air conditioners and one standby air conditioner in the equipment room | Four active air conditioners and two standby air conditioners in the module | Solution 3 has more standby air conditioners and features higher safety.
Conclusion: The in-row air conditioner + aisle containment solution is the optimal among the three solutions in terms of equipment room utilization rate, maximum power density of a single cabinet, PUE, and safety. The in-room + aisle containment solution is the second choice. The least recommended solution is the in-room air conditioner + open aisle solution.

## Slide 47: Advantages of the In-Row Cooling Mode
When designing a new data center, consider in-row cooling as the main cooling mode. Compared with the hybrid cooling architecture solution, the in-row cooling solution alone has more advantages.
  The raised floor is not required.
  The cabinet rows do not conflict with the cooling devices deployed around the room.
  The redundancy is simplified.
  Energy consumption costs are reduced.
  Maintenance expenses are reduced.
  Incompatibility between equipment from different vendors is reduced.
Notes: The raised floor is not required: Generally, the cooling devices around the room need to rely on the raised floor space for the air distribution of IT equipment. However, if in-row cooling devices are used to provide cooling for the entire room, the costs for installing and maintaining the raised floor can be avoided.
The in-row cooling devices do not conflict with those deployed around the room: When two cooling architectures are deployed in the same room, they may conflict with each other in terms of heating, cooling, humidification, and dehumidification. This will lead to lower operational efficiency and higher electricity bills. However, if only in-row cooling devices are used, and equipment can coordinate with each other, thereby avoiding such a conflict.
The initial investment is reduced: The combination of in-row cooling and cooling deployed around the room is too conservative, resulting in a huge waste of money. Using only in-row cooling devices to cool loads in the data center can reduce the cost by 50%.
The redundancy is simplified: If a data center needs to use the N+1, N+2, or 2N redundancy design, the cooling devices around the room do not require redundancy, saving more costs.
Energy consumption costs are reduced: Excessive additions to cooling devices often lead to higher energy consumption costs, which are more pronounced if the excess cooling devices are powered by constant-speed fans (commonly used in ceiling-mounted cooling devices around rooms).
Maintenance expenses are reduced: Using only in-row cooling devices eliminates the need of maintaining cooling devices around the room and reduces the OPEX of a data center.
Incompatibility between equipment from different vendors is reduced: When the hybrid design is used, the systems used are usually from different vendors. The more devices from different vendors are used, the more complex the data center O&M becomes.

## Slide 48
Load Introduction and Calculation for Data Center Cooling System
Air Conditioner Planning and Configuration for Data Center Cooling System
  Air Conditioner Configuration Principles and Selection of Data Center Cooling System
  Air Conditioner Planning and Configuration for Data Center Cooling System
  Air Supply Mode and Selection of Data Center Cooling System

## Slide 49: In-Row Cooling Solution
Key planning points for in-row air supply (commonly used in data centers): Determine the air conditioner type, whether cold aisle containment is used, and the unit positioning.
Air conditioner type
  DX in-row air conditioner (Consider the piping and drainage modes. If necessary, consider the raised floor mode.)
  Chilled water (CW) in-row air conditioner (Consider chilled water piping mode)
Precautions for unit positioning
Top piping | Bottom piping
No raised floor is required, and the layout is simple. Water pipes are routed from the top, which threatens equipment safety in case of water leakage. | 1. The raised floor is required. 2. Water leakage does not threaten equipment safety.
Ensure that there is no gap between cabinets.
Keep equipment load balance
Place the air conditioner in a proper position.
Avoid mixing of cold and hot air.
Notes: In-row air conditioners can be used if the power density is greater than 5 kW/rack.

## Slide 50: Characteristics of In-Row Air Supply
Characteristics of in-row air supply
  Close-coupled cooling and cold aisle form a cold-pool plenum to ensure even air supply.
  Better cooling distribution to ensure more even cooling and airflow
  Higher cost, lower PUE, and easy to deploy in phases
  Low requirements on the floor height. The raised floor is not mandatory.
  Applicable to medium- and high-density data centers with a power density greater than or equal to 5 kW/cabinet
In-row horizontal air supply (side view)
Air conditioner
Cabinet
Cabinet
Cabinet
Air conditioner
In-row horizontal air supply (top view)
Air conditioner
Cabinet
Cabinet
Cabinet
Air conditioner
Air conditioner
Cabinet
Cabinet
Cabinet
Air conditioner
Cold aisle containment

## Slide 51: In-Room Cooling Solution
Key planning points for in-room air supply: Determine the type and air supply mode of in-room air conditioners, whether to use cold aisle containment, air return mode, and unit positioning.
Air conditioner type
  DX in-row air conditioner
  CW in-row air conditioner
Air supply mode
  Upflow: Consider air cap and air duct configurations.
  Downflow: Estimate and determine the height of the raised floor, whether aisle containment is used, and the air return mode.

## Slide 52: In-Room Cooling Solution – Upflow
Key planning points of upflow: Air cap vs. Air duct (rarely used in new data centers)
Upflow using air caps
  Advantages: simple construction, low cost, and short air supply distance. Generally, the air supply distance of the air conditioners is less than or equal to 25 m.
  Disadvantage: poor uniformity of the temperature field
  The noise is loud.
  Applicable to: small- and medium-sized data centers where the air supply distance of a single air conditioner is less than 25 m
Upflow using air ducts
  Advantages: long air supply distance and even air supply
  Disadvantages: high construction cost and complex engineering. Enough floor height of a data center is required (the air duct is 500 mm thick).
  Applicable to medium- and large-sized data centers that have high requirements for air conditioners or use air caps to supply air unconditionally. Select a proper external residual pressure based on the distance between air ducts.

## Slide 53: In-Room Cooling Solution – Downflow
Key planning points for underfloor downflow (commonly used in data centers): Estimate and determine the height of the raised floor, whether aisle containment is used, and the air return mode.
Aisle containment
  Generally, it is recommended that the cold and hot aisles be used if the power density of a data center is 1–4 kW/rack to meet equipment requirements.
  If the power density is greater than 4 kW/rack, cold or hot aisle containment is recommended. Currently, cold aisle containment is more widely used than hot aisle containment.
Return air type
Return Air Type | Characteristic
Free air return | If the return air efficiency of the data center is low, the overall temperature of the data center will be high. Therefore, when power cables are routed from the top, the air return vent of the air conditioners must be located under the power cables to prevent the power cables from blocking the hot air return.
Air return from the ceiling | The return air vent is set on the suspended ceiling of the hot aisle. In this way, the hot air is guided, and the cold and hot air cannot be mixed easily. As a return air plenum, the suspended ceiling ensures a stable and efficient return air process.

## Slide 54: Comparison Between Upflow and Downflow Applications
Which of the two air supply modes is more reasonable? The analysis is as follows.
Assume that there are 17 cabinets in each row of the cold aisle and hot aisle in a data center. The cooling load of each cabinet is 3.8 kW. The total cooling load of the two rows of cabinets on both sides of the cold aisle is: 17 x 2 x 3.8 = 129.2 kW.
Air supply diagram 1
Air supply diagram 2

## Slide 55: Upflow
Upflow solution overview
Calculation of the air duct size and wind speed:
  For upflow, the width of the air ducts is equal to the width of the cold aisle, which is generally 1.2 m. The height of the air ducts is 0.75 m. Therefore, the cross-sectional area of the air ducts is: 1.2 x 0.75 = 0.9 m2.
  In a precision air conditioning system, the air volume required for every 1 kW cooling capacity is about 270 m3/h. Therefore, the maximum air volume in a single air duct above the cold aisle is: 129.2 x 270 = 34,884 m3/h, and the wind speed is: 34,884/(0.9 x 3600) = 10.8 m/s. When the wind speed is higher than 5 m/s, high noise is generated in the air ducts. Therefore, the noise generated by the wind speed of 10.8 m/s will severely affect the internal working environment of a data center.
  When the wind speed in the air ducts is high, the cross-sectional area of the air ducts must be changed to ensure that the wind speeds at the local and remote air vents of the air ducts are consistent. To implement the variable cross-sectional area design of the air ducts, the power of each cabinet of the two rows must be obtained. However, the power of each cabinet cannot be accurately obtained during the design of a data center, and the power of each cabinet cannot be ensured to remain unchanged for decades.
Conclusion: According to the impact on the environment, the upflow solution is not suitable when the wind speed is higher than 5 m/s.
Notes: When the upflow mode is used, cabinets are installed in rows on the hard floor. Air supply ducts are deployed above the cold aisles, and cable trays are deployed above the cabinets.

## Slide 56: Downflow
Downflow solution overview
Calculation of the air duct size and wind speed:
  When the downflow mode is used, the space under the raised floor can house a large plenum. Cold air enters the plenum from the air conditioners, and then is sent to the cold aisle in the front of the cabinet through the air supply vent on the floor. The size of the plenum can be selected as required.
  The width of the two rows of cabinets is 3.6 m. If the net height of the floor is 0.75 m, the maximum wind speed under the floor is: 34,884/(3.6 x 0.75 x 3600) = 3.58 m/s when the downflow mode is used. Therefore, compared with the upflow mode, the wind speed is significantly reduced.
  In the downflow mode, the air vent floor with adjustable ventilation rate is used. The ventilation area and wind speed of the front air vent floor of each cabinet are adjusted to provide proper air volume based on the cabinet requirements.
Conclusion: The downflow mode has low wind speed and is easy to achieve on-demand air supply.
Notes: If the indoor net height of the building where the data center is located meets the requirements, adopt the air return mode using space above the suspended ceiling. In this way, the ineffective mixing of cold air and hot air is reduced as much as possible, and the efficiency of the air conditioning system is improved.

## Slide 57: Conclusion
Assume that there are 17 cabinets in each row of the cold aisle and hot aisle in a data center. The cooling load of each cabinet is 3.8 kW. The total cooling load of the two rows of cabinets on both sides of the cold aisle is: 17 x 2 x 3.8 = 129.2 kW.
Item | Air Duct Size | Wind Speed | Air Supply Evenness | Noise Level | Aesthetics
Upflow | Large | High | Poor | High | Poor
Downflow | Standard | Low | Adjustable | Low | Good

## Slide 58: Underfloor Downflow vs. In-Row Air Supply
There are two modes of airflow organization in data centers: underfloor downflow and in-row air supply. The following table lists the comparison between the two modes.
In the process of selecting the indoor airflow organization for a data center, in-row air supply as well as downward air supply and upward air return are the most commonly used air supply modes.
Generally, the underfloor downflow mode is used in scenarios with low power density (lower than 8 kW/rack), and the in-row air supply mode is used in scenarios with high power density.
Item | Downward Air Supply and Upward Air Return (Data Center) | In-Row Air Supply (Data Center)
Hot spot probability | Changes in the cabinet power density may cause hot spots. | Changes in the cabinet power density can be adjusted by means of cooling capacity sharing to reduce the possibility of hot spots.
Airflow mixing | If the aisle is not sealed, cold and hot airflows may be mixed, reducing the cooling effect. | Close to the heat source, short air supply distance, and good cold and hot partition prevent the possibility of airflow mixing.
Cooling capacity allocation | The pressure of underfloor downflow depends on the equipment room dimensions and floor depth. During design and selection, ultra-large models are used to ensure reliability. | The cooling requirement and cooling capacity can be accurately matched without over-planning.
Application scenarios | Applicable to the scenario where the cabinet power density is low | Applies to scenarios where the power density is greater than 5 kW/rack, especially greater than 8 kW/rack.

## Slide 59: Recommended Air Supply Solution
The underfloor downflow mode is not flexible, and the cooling effect is poor when the power density is high. Therefore, this mode applies to low-density scenarios. The in-row air supply mode applies to modular layouts and high-density scenarios.
Before selecting an air supply solution, determine the air supply mode first: underfloor downflow or in-row air supply. Then select an appropriate air supply solution based on the cabinet power density. For details about how to select a proper air supply solution, see the following table.
Scale | Power Density (kW/Rack) | Air Supply Solution
Small-sized data center | 1 ≤ P ≤ 5 | Underfloor downflow + Cold and hot aisle (unsealed)
Medium-sized data center | 5 < P ≤ 8 | Underfloor downflow + Cold aisle containment
 |  | Underfloor downflow + Cold aisle containment
Large-sized data center | 5 < P ≤ 15 | In-row air supply + Cold/Hot aisle containment

## Slide 60: Return Air Solution in Free Air Supply Mode
In-room cooling
Small-sized network equipment room (power consumption less than 40 kW):
Not recommended for most data centers
Low cost
The energy efficiency is the lowest in all airflow distribution architectures because all cold airflows will be mixed with hot return air. The supply air temperature is difficult to predict.
Racks with a maximum cooling power consumption of 4 kW can be cooled.
General-purpose equipment room (power consumption less than 40 kW):
Not recommended for most data centers
Low cost and easy installation
It is more energy efficient than free air return, because 40–70% of the IT hot return air will be captured and transferred back to the cooling equipment. The air supply temperature is more predictable than free air supply due to less mixing of hot air and cold air.
Racks with a maximum cooling power consumption of 8 kW can be cooled.
Large-sized or hosting data center:
The energy efficiency is the highest in all airflow distribution architectures because the architecture allows high supply air temperature of cooling equipment, which increases the duration of free cooling.
70–100% of the IT exhaust hot air will be captured and transferred back to the cooling equipment. The air supply temperature is the most predictable because hot air is not mixed with cold air.
Free air return
Precise air return
Air return with airflow containment

## Slide 61: Return Air Solution in Precise Air Supply Mode
In-room cooling
Data center with constant power density:
Not recommended for new data centers because the predictable power density cannot be met.
It is more energy efficient than free air supply because more hot air is transferred back to the cooling equipment.
Racks with a maximum cooling power consumption of 6 kW can be cooled.
Small and medium-sized data center:
It is more energy efficient than free air return, because 60–80% of the IT hot return air will be captured and transferred back to the cooling equipment. The air supply temperature is more predictable than free air supply due to less mixing of hot air and cold air.
Racks with a maximum cooling power consumption of 8 kW can be cooled.
High-temperature rack:
It has higher energy efficiency than precision air supply and return because 70–100% of the IT hot return air will be captured and transferred back to the cooling equipment. The air supply temperature is the most predictable because hot air is not mixed with cold air.
Higher supply air temperature for cooling equipment is supported, thereby increasing the duration of free cooling.
Racks with a maximum cooling power consumption of 30 kW can be cooled.
Free air return
Precise air return
Air return with airflow containment

## Slide 62: Raised Floor Height
Impact of raised floor height
  In the underfloor downflow mode of a data center, the height of the raised floor affects the height of the equipment room floor and further affects the initial investment in civil work.
  The distribution of the underfloor downflow speed and pressure is also affected, which affects the cooling effect of the server.
Distribution of air volume of the floor grilles in
different heights of raised floors
The height of the raised floor ranges from 400 mm to 1000 mm, and the air volume decreases gradually. This indicates that the difference between the air volume of the floor grilles in the equipment room decreases with the rise of the raised floor.
Height (mm)
Air volume (m3/s)
Notes: In a proper scale, try to select a higher floor.
In the preceding figure, the height of the raised floor is the only variable. Seven groups of raised floor heights (400 mm, 500 mm, 600 mm, 700 mm, 800 mm, 900 mm and 1000 mm) are selected for comparison and analysis. Five typical cross-sectional areas and the temperature of the entire equipment room are selected for comparison and analysis.

## Slide 63: Air Supply Grille Porosity
Impact of underfloor downflow grille porosity
  The objective of data center cooling is to ensure that the server inlet temperature does not exceed the maximum allowable inlet temperature. The main cause of the high inlet temperature of the cabinet server is that the cooling airflow through the floor grilles is insufficient. As a result, the server sucks in the hot air from the hot aisle and forms hot spots.
As the porosity of the floor grilles decreases, the unevenness of the air volume of the floor grille in the equipment room decreases.
Air volume (m3/s)
Distribution of air volume in floor grilles
Porosity
Notes: The preceding figure shows the distribution of the air volume in floor grilles. The longer the red bar, the worse the evenness of air exhaust.

## Slide 64: Underfloor Downflow – Cold/Hot Aisle Containment
Cold aisle containment indicates that the two ends and top of the cold aisle are sealed. The cold air passes through the cabinet server and then returns to the air conditioners through the air return vent for cooling. Hot aisle containment refers to installing pipes on the hot aisle to lead the hot air discharged by the cabinet server to the suspended ceiling and then to the air conditioners for cooling.
Underfloor downflow – cold and hot aisle containment
Notes: When the hot aisle is sealed, cold air can be transferred from any position in the equipment room to the cabinet server. Therefore, there is no requirement on the raised floor. For the airflow distribution mode of raised floor air supply, the cold aisle containment is more economical, efficient, simple, and easy to implement. The cold/hot aisle containment can prevent mixing of cold and hot air, reduce the intake air temperature of cold air, and reduce partial overheating. As the mixing of cold air and hot air is reduced, the temperature difference between the supply air and return air is increased, and the cooling efficiency of the air conditioning system is improved. For data centers with a power density of 4–8 kW/rack, aisle containments must be considered.

## Slide 65
Selection of the air conditioner type of the data center air conditioner
Equipment room layout and selection of air conditioners
Air supply mode and selection of data center air conditioners
Data center load type
Cooling load calculation of data centers
Cooling load estimation method

## Slide 66
Answer the following questions:
How are the air conditioners configured in redundancy mode in a data center?
Why does the cooling load calculation of data centers include the redundancy coefficient?
Notes: 1. The N+1 or N+X mode varies depending on customer requirements and data center levels.
2. The cooling loss and other impacts are considered.

## Slide 68
HCIE-DCF-Design
V1.0
Yuewenjun/wx507858
2020/10/7
Lishaofeng/00486775
2020/12/7