## Slide 1: Data Center Chilled Water Air Conditioning System Configuration

## Slide 2
This course introduces components, configuration principles and methods, and energy saving configuration methods of the chilled water air conditioning system in a data center.

## Slide 3
On completion of this course, you will be able to:
  Get familiar with the configuration methods of chilled water air conditioners in a data center.
  Understand the air conditioner water system types and their application scenarios.
  Calculate the air conditioner configuration based on actual projects.
  Study the feasibility of the chilled water air conditioning system.

## Slide 4
Chilled Water Air Conditioner Planning Overview
Chilled Water System Configuration
Cooling Water System Configuration

## Slide 5: Chilled Water Air Conditioning System Components
Chilled water system: consists of chillers, transmission pipes, chilled water pumps, indoor units, valves, and other accessories.
Cooling water system: consists of cooling towers, transmission pipes, cooling water pumps, valves, and other accessories.
Condensate water system: consists of transmission pipes, drainage pumps, etc.
Cooling water system
Chilled water system
Data center airflow organization
Refrigerant system
Notes: Cold (hot) water system: provides cold (hot) water for air handling units.
Cooling water system: provides cooling water for the condenser of a water-cooled chiller.
Condensate water system: discharges air condensate water.

## Slide 6: Configuration Design Process for the Chilled Water Air Conditioning System
Accept a design task
Input requirement parameters
Determine air
conditioning system type
Calculate cooling load
Design air flow organization form
Select indoor units
Select chilled water equipment
Select cooling water equipment
Calculate air pipes and water pipes
Draw construction drawings
Complete the design task

## Slide 7
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
  Air Conditioner Chilled Water System Classification
  Chiller Calculation and Selection
  Chilled Water Pump Calculation and Selection
  Data Center Air Conditioner Water System Configuration
Cooling Water System Configuration

## Slide 8: Chilled Water System Classification
The chilled water system is a bridge between the cooling source and the indoor units. It is better to consume less energy in transmission. Therefore, the proper design and configuration of the chilled water system ensure the safe and economical operation of the air conditioning system in a data center.
The chilled water system needs to be determined based on the project scale, data center function requirements, climatic conditions, cooling sources, pumps, and indoor units. After technical and economic comparison, the chilled water system can be designed as an air conditioning system with different pipe types and adjustment modes.
In the air conditioning engineering, air conditioning systems can be classified from different perspectives. There are five classification bases: circulation mode, water supply and return mode, pipe distribution mode, operation adjustment mode, and circulating pump configuration mode. In the actual design of the air conditioning system, these different bases need to be considered to select the air conditioning system suitable for the actual project.

## Slide 9: Chilled Water System Classification - Open and Closed Systems
Open and closed systems
  Open system
    The pump has a high lift and energy consumption.
    Circulating water is easily polluted.
    The water return tank has the cold storage capacity.
  Closed system
    The pump has a low lift and energy consumption.
    Circulating water is not easily polluted.
Open system
Closed system
Chiller
Circulating water pump
Water return tank
Air conditioner indoor unit
Air conditioner indoor unit
Chiller
Circulating water pump
Expansion water tank
Notes: Open system: There is a water tank or pool between pipes to ventilate. When water flows back, the pipes ventilate.
  Advantages: The chilled water tank has the cold storage capability, which can reduce the turn-on time of a chiller and increase the energy adjustment capability. The chilled water temperature fluctuates slightly.
  Disadvantages: When chilled water contacts with the air, high oxygen content in circulating water is easy to corrode pipes. In addition to overcoming the pipe resistance, the head of the water pump should be able to lift water to a certain height. Therefore, the lift and energy consumption of the water pump are relatively high. If self-flowing return water is used, the diameter of the return water pipe is large, which will increase the investment.
  Application scenarios: The air conditioning system sprays water to cool the air. The temperature fluctuation of chilled water is small or the energy adjustment of a chiller cannot adapt to the change of the air conditioning system. The open tank is used to store chilled water to reduce the peak load. The cooling water system with a spray cooling tower is used.
Closed system: Water in pipes does not contact with the air. An expansion water tank is installed only at the highest point of the system.
  Advantages: Pipes do not contact with the air, and pipes and equipment are not easily corroded. The lift required by a pump is determined only by the pipe resistance and does not need to overcome the hydrostatic pressure. The lift and power of the pump are low. The system is simple.
  Disadvantages: Its cold storage capacity is weak. When the load is low, the chiller needs to be started frequently. Sometimes, a pressurized water pump is required to refill water to the expansion water tank.
  Application scenarios: The air conditioning system uses fan coil units, inducers, and water-cooled surface coolers. An air-conditioning cold water system for high-rise buildings is used. A hot water system is used.

## Slide 10: Chilled Water System Classification - Two-Pipe, Three-Pipe, and Four-Pipe Systems
Two-pipe, three-pipe, and four-pipe systems
  Two-pipe system: only has a water supply pipe and a water return pipe.
  Three-pipe system: has a cold water supply pipe, a hot water supply pipe, and a water return pipe.
  Four-pipe system: has cold and hot water supply and return pipes.
One supply and one return, winter-summer switching
Two-pipe system
Cold and hot water supply, one return
Three-pipe system
Cold and hot water supply, cold and hot water return
Four-pipe system
Cold and hot water supply, cold and hot water return
Four-pipe system
Cold and hot water FCUs
Mono fan coil unit (FCU)
Notes: Two-pipe system
  The system has only a water supply pipe and a water return pipe. It circulates cold water in summer and hot water in winter, and uses valves to switch between them.
  The two-pipe system is simple and easy to construct. The initial investment is low, but it cannot be used in places that require both cold and hot water supply.
  According to GB 50736-2012, when all areas in a building require simultaneous cold and hot water supply switching only by season, the two-pipe system should be used.
Three-pipe system
  The system has a cold water supply pipe, a hot water supply pipe, and a water return pipe. The cold water and hot water share one water return pipe.
  The system can supply cold and hot water simultaneously. Compared with the four-pipe system, it is simpler. However, the system is more complex than the two-pipe system and requires higher investment. In addition, the three-pipe system has the loss of mixing the cold and hot water return.

## Slide 11
Notes: Four-pipe system
  In the system, separate water supply pipes and water return pipes are set for cold water and hot water to form two sets of independent water supply and return pipes for cooling and heating respectively.
  The system can supply cold and hot water simultaneously, which meets the requirements of high-quality air conditioning environment. However, the system is complex, requiring high initial investment and more building space.
  According to GB 50736-2012, when the cold and hot water supply needs to be frequently switched or used simultaneously, the four-pipe system is recommended.
Zone-based two-pipe system
  Based on the load characteristics of air conditioning areas in buildings, air conditioning water pipes are classified into the two-pipe cold water system and two-pipe cold-hot water system. For areas that require cooling throughout the year, the two-pipe cold water system is used. For other areas, the two-pipe cold-hot water system is used.

## Slide 12: Chilled Water System Classification - Reversed and Direct Return Systems (1)
Reversed and direct return systems
  In the reversed return system, the pipe distance of the water flow passing through each parallel loop is basically the same, so the resistance loss of each pipe is nearly the same.
Two layout modes of main vertical pipes in the reversed return system
Two layout modes of branch horizontal pipes in the reversed return system
Expansion water tank
Expansion water tank
Heat
exchanger
Heat
exchanger
Heat
exchanger
Heat
exchanger
Heat
exchanger
Circulating water pump
Chiller
Circulating water pump
Chiller
Return water
Supply water
Supply water
Return water
Heat
exchanger
Heat
exchanger
Heat
exchanger
Notes: Advantages of the reversed return system: When the water resistance of each terminal heat exchanger is approximately the same, the total pipe length of each parallel loop is basically the same. Therefore, the reversed return system has good hydraulic stability and balanced water distribution among loops, and is convenient to be adjusted.

## Slide 13: Chilled Water System Classification - Reversed and Direct Return Systems (2)
Reversed and direct return systems
  In the direct return system, the distance of the water flowing through the pipes in each parallel loop is unequal, so the resistance is unequal.
Main vertical pipes in the direct return system
Branch horizontal pipes in the direct return system
Chiller
Expansion water tank
Heat exchanger
Circulating
water pump
Heat
exchanger
Heat
exchanger
Heat
exchanger
Supply water
Return water
Notes: Advantages of the direct return system: Simple pipe configuration, less pipe material consumption, less construction difficulty, and lower investment.
Disadvantages of the direct return system: The total pipe length of the parallel loops is unequal, and the resistance between the loops is not balanced, which leads to uneven flow distribution.

## Slide 14: Chilled Water System Classification - Constant and Variable Flow Systems
Constant and variable flow systems
  Constant flow system: The water flow is constant. The temperature difference between the supply and return water is changed to adapt to the change of the load.
  Variable flow system: The temperature difference between the supply and return water remains unchanged. The water flow is changed to adapt to the change of the load of the air conditioner. The water flow varies with the load.
Three-way valve adjustment diagram
Two-way valve adjustment diagram
Indoor unit
Heat sensor
Three-way valve
Two-way valve
Indoor unit
Heat sensor
Notes: Constant flow system: When the load decreases, the temperature difference between the supply water and return water of the water system decreases. As a result, the energy transmitted to the load by the system decreases to meet the load reduction requirements. However, the transmission energy consumption of the water system does not decrease. Therefore, the water transmission efficiency decreases.
  The constant flow system works as follows: An electric three-way valve is used to adjust each air conditioner indoor unit of the system. When the room temperature does not reach the set value, the straight-through pipe of the three-way valve is opened, the bypass pipe is closed, and the supply water passes through the indoor units. When the room temperature reaches or exceeds the preset value, the straight-through pipe is closed and the bypass pipe is opened. All water flows into the water return pipe through the bypass pipe. Therefore, the water flow on the load side is constant.
  Advantages of the constant flow system: It is simple and convenient and does not need more complex automatic control equipment. The three-way valve is used to adjust the water flow at the user end. Users do not interfere with each other, and the system runs stably.
  Disadvantages of the constant flow system: The water flow of the system is determined by the maximum load. The water supply volume is greater than the required water volume in most time. The energy consumption of the transmission is always in the maximum value, and the ineffective energy consumption of a pump is high.

## Slide 15
Notes: Variable flow system: When the load decreases, the system water flow decreases accordingly, so that the system delivers less energy to the load to meet the load reduction requirement. Because the reduction of water flow can reduce the energy consumption of water transportation, energy can be saved greatly.
  The variable flow system works as follows: Each air conditioner indoor unit of the variable flow system is regulated by an electric two-way valve. When the room temperature does not reach the set value, the two-way valve is opened fully or greatly, and the water flow through the indoor units increases. When the room temperature reaches or exceeds the set value, the two-way valve is closed fully or greatly, and the water flow through the indoor units decreases. Therefore, the water flow rate on the load side is variable.
  Advantage of the variable flow system: The energy consumption of pumps decreases with the decrease of load (energy saving). In piping system design, the simultaneous-use coefficient can be considered. The pipe diameter is smaller, and the initial investment of the pumps and pipes decreases.
  Disadvantage of the variable flow system: The control device of the variable flow system has high requirements and is complex.

## Slide 16: Chilled Water System Classification - Primary and Secondary Pump Systems
Primary and secondary pump systems
  Primary pump system: In the system, the cooling source side and the load side share a group of circulating water pumps.
Primary pump system diagram
Primary pump? Secondary pump?
Expansion water tank
Two-way valve
Terminal heat exchanger
Bypass valve
Main water supply pipe
Main water return pip
Chilled water pump
Chiller
Notes: The primary pump system works as follows: The system uses a bypass pipe to maintain the constant flow of the cooling source side and let the load side in variable flow operation. A differential pressure bypass device is set between the main chilled water supply and return pipes. When the air conditioner load decreases, the resistance of the pipe on the load side increases, and the differential pressure control device automatically increases the opening of the bypass valve. The reduced water flow on the load side returns to the main water return pipe from the bypass pipe and flows back to the chiller. Therefore, the water flow of the chiller evaporator is always constant.
  Advantages and disadvantages of the primary pump system
    Advantages: The system is simple with few control components, so it is easy to operate and manage
    Disadvantages: The water flow adjustment is restricted by the minimum water flow rate of the chiller. The system is unsuitable when there is a great gap between the water supply radius and lift of each zone. Therefore, it can only be used in small and medium air conditioning systems.

## Slide 17: Chilled Water System Classification - Primary and Secondary Pump Systems
Primary and secondary pump systems
  Secondary pump: In the secondary pump system, circulating water pumps are configured on the cooling source side and load side.
The secondary pump system consists of two loops:
  Primary loop: main water return pipe → primary pump → chiller → main water supply pipe. The primary loop is responsible for the preparation of chilled water.
  Secondary loop: main water supply pipe → secondary pump → indoor unit → main water return pipe. The secondary loop is responsible for the transmission and distribution of chilled water.
Secondary pump system diagram
Expansion water tank
Two-way
valve
Terminal heat exchanger
Bypass valve
Main water return pipe
Secondary pump
Balance pipe
Main water supply pipe
Primary pump
Chiller
Chiller
Notes: Advantages and disadvantages of the secondary pump system
  Advantages: The system can adapt to the situation that the load change regularity of each zone is different and the loop lift or water supply radius of each zone is greatly different. It can realize variable flow of the secondary pump and save energy consumption of transportation.
  Disadvantages: The system is complex and has high requirements on control devices. It also requires a large floor area of a data center and high initial investment.

## Slide 18: Chilled Water System Classification - Primary and Secondary Pump Systems
Hybrid system of primary and secondary pumps
  In the transmission and distribution loop of the chilled water, the loop with short pipes and small pressure loss is directly supplied by the primary pump, and the loop with large pressure loss is supplied by the secondary pump. In this way, a hybrid system of the primary and secondary pumps is formed.
Expansion water tank
Two-way
valve
Terminal heat exchanger
Main water supply pipe
Main water return pipe
Chiller
Chiller
Balance pipe
Secondary pump
Primary pump

## Slide 19: Chilled Water System Classification Basis and Key Design Points
Classification Basis | Water System Types | Key Design Points
Circulation mode | Open circulation system | The pump lift of the open system is high. An open system must be configured with a chilled water storage tank. A closed system must be configured with an expansion water tank.
 | Closed circulation system | 
Water supply and return mode | Two-pipe system | The number of water system equipment suites to be configured varies with the water supply and return modes. The more the number of pipes, the more complex the layout of the pipes in design.
 | Three-pipe system | 
 | Four-pipe system | 
 | Zone-based two-pipe system | 

## Slide 20: Chilled Water System Classification Basis and Key Design Points
Classification Basis | Water System Types | Key Design Points Comparison
Water supply and return pipe layout | Reversed return system | The pipes of the reversed return system are long and the layout is complex. The reversed return system needs to be configured with a higher water pump lift. The resistance balance of the parallel pipes should be taken into account during the design of the direct return system.
 | Direct return system | 
Operation adjustment mode | Constant flow system | The constant flow system can be configured with constant frequency pumps. The variable flow system must be configured with variable frequency pumps. Chillers with strong adaptability to flow change should be selected for the variable flow system. The variable flow system needs to be equipped with a complex control system.
 | Variable flow system | 
Circulating pump configuration mode | Primary pump system | The primary pump system needs to be equipped with water pumps only on the cooling source side. The secondary pump system needs to be equipped with pumps on both the cooling source side and the user side.
 | Secondary pump system | 
Notes: The primary pump system is divided into the primary pump constant flow system and variable flow system.
The secondary pump system is usually a variable flow system with a variable frequency pump on the load side and a constant frequency pump on the cooling source side.

## Slide 21
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
  Air Conditioner Chilled Water System Classification
  Chiller Configuration and Selection
  Chilled Water Pump Configuration and Selection
  Data Center Air Conditioner Water System Configuration
Cooling Water System Configuration

## Slide 22: Chiller Type Selection
Piston chiller
Screw chiller
Centrifugal chiller
Steam lithium bromide absorption chiller
Direct-fired lithium bromide absorption chiller
Heat pump chiller for both cooling and heating
Piston chiller
Screw chiller
Centrifugal chiller
Lithium bromide absorption chiller
Water source heat pump
Air-cooled heat pump
Notes: Comparison should be made before chiller selection. Electric compression chillers and lithium bromide absorption chillers should be compared.
If the power supply is tight or the electricity price is high but there is gas supply, the direct-fired lithium bromide absorption chiller is recommended.
The air-cooled or buried pipe ground source chiller is recommended to supply chilled water to small and medium buildings in hot summer and cold winter areas and arid areas.
Air-cooled chiller: It is applicable to office buildings having flexible construction and scattered small rooms but without basements or dedicated refrigeration rooms.
Heat pump chiller (water source, air source): It is applicable to buildings that require both cooling and heating air conditioners.

## Slide 23
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
  Air Conditioner Chilled Water System Classification
  Chiller Calculation and Selection
  Chilled Water Pump Calculation and Selection
  Data Center Air Conditioner Water System Configuration
Cooling Water System Configuration

## Slide 24: Chilled Water Pump and Chiller Configuration Mode
One-to-one mapping between primary pumps and chillers
Parallel mapping between primary pumps and chillers
Circulating water pump
Chiller
One chiller to one pump, no standby pump, the chillers are connected first in series and then in parallel
One chiller to one pump, standby pumps are set, the chillers are connected first in series and then in parallel
Circulating water pump
Chiller
Circulating water pump
Chiller
Shared manifold
One chiller to one pump, no standby pump, the chillers are connected first in parallel and then in series
Normally closed manual change-over valve
Normally closed manual change-over valve
Notes: One-to-one mapping between primary pumps and chillers
  Advantages: Chillers with different flow can be connected in parallel for working. The flow between the pump and the chiller (evaporator) is easy to match. When the load changes, the chiller with the corresponding flow can be started to avoid the waste of energy caused by the large chiller with small loads.
  Disadvantage: Pumps cannot be used as backups for each other.
Parallel mapping between primary pumps and chillers
  According to GB 50736-2012 Design Code for Heating Ventilation and Air Conditioning of Civil Buildings, when it is difficult to configure one pump for each chiller, a shared manifold can be used. In this case, an electric two-way valve needs to be installed between the chiller and the circulating water pump for separation.
  Advantage: If the pumps connected in parallel are the same, any one of the pumps in the parallel pump group can be used as a standby pump.
  Disadvantage: When the chillers or pumps have different sizes, it is difficult to match the flow between the pumps and the chillers (evaporators). Starting or stopping chillers will have a negative impact on the running chillers.

## Slide 25: Chilled Water Circulating Pump Flow Calculation
Calculate the flow of the circulating water pump as follows:
  Types: Horizontal double suction pump or horizontal end suction pump
  System type: Primary or secondary chilled water pump system
  The formula for calculating the flow of a circulating water pump is as follows:
  G = K * Q/ (1.163Δt) = 0.86 * K * Q/Δt
  G: pump flow (m3/h)
  Q: cooling (heating) load (kW) of the pump
  K: additional flow coefficient of the pump. The value ranges from 1.05 to 1.1.
  Δt: temperature difference between supply and return water (°C)
Horizontal centrifugal pump
Vertical centrifugal pump
Notes: Generally, the single suction pump is used. If the flow is greater than 500 m3/h, the double suction pump is recommended.
In addition to small units such as modular units and the primary pump variable flow system, the number of circulating water pumps in the primary pump system and the number of primary pumps in the secondary pump system should be consistent with the number and flow of chillers.
The secondary cold water pump in the secondary pump system should be determined based on system zoning, the flow and the operation adjustment mode of each zone. At least two secondary cold water pumps should be deployed in each zone, and the variable frequency speed regulating pump should be used.

## Slide 26: Chilled Water Circulating Pump Lift Calculation
The lift of a circulating water pump should be calculated as follows:
  The calculation method of an open system is different from that of a closed system. Using the closed system as an example, the lift calculation formula is as follows:
  H = K * ∑△h
  K: additional safety factor, ranging from 1.05 to 1.1
  ∑△h: total pipe resistance loss
For a closed water system:
  ∑△h = Hf + Hd + Hm.
  Hf and Hd: the loss due to frictional resistance and local resistance of the water system respectively (Pa)
  Hm: equipment resistance loss (Pa)
Note: Detailed hydraulic calculation is required.
Notes: Primary pump system:
  For the closed circulation system, the pump lift should be calculated based on the sum of the resistance of pipes and pipe fittings, the resistance of the self-control valve and filter, the resistance of the chiller evaporator (or heat exchanger), and the resistance of the indoor unit heat exchanger.
  In addition to the preceding resistance, the pump lift of the open system should also include the height difference between the lowest water level of the water storage tank or chilled water storage tank and the indoor unit. If a spray chamber is deployed, the resistance of the indoor unit heat exchanger should be replaced by the necessary pressure head in front of the nozzle.

## Slide 27
Notes: Secondary pump system:
  The lift of the primary pump in the closed circulation system should be calculated based on the sum of the resistance of the pipe and pipe fittings on the cooling source side, the resistance of the self-control valve and filter, and the resistance of the chiller evaporator.
  In addition to the resistance described in item 1, the lift of the primary pump of the open system should include the height difference between the lowest water level of the water storage tank or chilled water storage tank and the chiller evaporator.
  The lift of the secondary pump in the closed circulation system should be calculated based on the sum of the resistance of the pipe and pipe fittings on the load side, the resistance of the self-control valve and filter, and the resistance of the indoor unit heat exchanger.
  In addition to the resistance described in item 3, the lift of the secondary pump in the open system should also include the height difference between the lowest water level of the water storage tank or chilled water storage tank and the indoor unit. If there is a spray chamber, the resistance of the indoor unit heat exchanger should be replaced by the necessary pressure head in front of the nozzle.

## Slide 28: Chilled Water Circulating Pump Lift Estimation
Chilled water pump lift components (can be used for drawing or equipment reviewing)
  Water resistance of the chiller evaporator: generally 5 to 7 mH2O (For details, see the product sample.)
  Water resistance of the surface cooler or evaporator of the indoor unit (such as precision air conditioner or FCU): generally 5 to 7 mH2O (For details, see the product sample.)
  Resistance of the return water filter: generally 3 to 5 mH2O
  Water resistance of water distributors and collectors: generally 3 mH2O
  Loss due to water pipe friction resistance and local resistance loss of the cooling system: generally 7 to 10 mH2O
To sum up, the lift of the chilled water pump ranges from 26 to 35 mH2O. Generally, the lift ranges from 32 to 36 mH2O.
Note: In the specific design phase, the lift must be calculated based on the actual situation of the cooling system. Do not copy the empirical value.
Evaporator
Indoor unit
Return water filter
Notes: Generally, distribution manifolds are designed at the water supply and return outlets of the chilled water unit to connect pipes to each area.

## Slide 29
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
  Air Conditioner Chilled Water System Classification
  Chiller Calculation and Selection
  Chilled Water Pump Calculation and Selection
  Data Center Air Conditioner Water System Configuration
Cooling Water System Configuration

## Slide 30
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
Cooling Water System Configuration
  Cooling Water System Overview
  Cooling Tower Configuration and Selection
  Cooling Water Pump Configuration and Selection

## Slide 31: Cooling Water System Concept
The cooling water system uses a cooling tower to supply circulating cooling water to the condenser of a chiller. The system consists of the cooling tower, cooling water tank, cooling water pump, condenser, and connection pipes.
Cooling tower
Refill water
Dosing device
Cooling water pump
Rooftop
Chiller
Dirt remover
Notes: If the air-cooled chilled water air conditioning system is used, the cooling water system is not required.

## Slide 32: Cooling Water System Types
One-to-one configuration of pumps, chillers, and cooling towers
  Advantages: The cooling water system of each chiller is independent of each other. The systems are subject to coordinated control for flow matching. Balance pipes are not required between cooling towers.
  Disadvantages: The pipeline layout is complex, the number of pipes and the space they occupy are large. Therefore, pipes cannot back up each other.
Pump, chiller, and cooling tower configurations
Cooling water pipe configuration where pumps, chillers, and cooling towers are connected in parallel respectively
  Advantages: No standby device is required. Few pipes are used and the investment is small.
  Disadvantages: When the sizes of chillers (condensers) are different, it is difficult to match the cooling water flow between equipment.
Pipe configuration where water pumps, chillers, and cooling towers are connected in parallel respectively
Chiller
Chiller
Chiller
Valve
Valve
Valve
Cooling water pump
Cooling water pump
Cooling water pump
Cooling tower
Cooling tower
Cooling tower
Fan
Fan
Fan
Chiller
Chiller
Chiller
Valve
Valve
Valve
Cooling water pump
Cooling water pump
Cooling water pump
Cooling tower
Cooling tower
Cooling tower
Fan
Fan
Fan
Control valve
Control valve
Control valve
Notes: Balance pipe
SRS: Automatic scale removal system for cooling water

## Slide 33: Cooling Water System Types
Cooling water pipeline with a main water supply pipe and a main water return pipe
  A balance pipe is installed between the water pans of each cooling tower so that the cooling towers run at the same water level. This prevents water level inconsistency between water pans of each cooling tower and avoids water overflow of some cooling towers and water refilling of other cooling towers.
Cooling water pipeline with a main water supply pipe and a main water return pipe
Chiller
Chiller
Chiller
Valve
Valve
Valve
Cooling water pump
Cooling water pump
Cooling water pump
Cooling tower
Cooling tower
Cooling tower
Main water supply pipe
Main water return pipe
Balance pipe
Balance pipe
Control valve
Control valve
Control valve
Notes: The following methods are recommended to solve uneven flow distribution:
  Electric two-way valves are installed on the branch water return and supply pipes of cooling towers. The two sets of valves operate as a pair and are electrically interlocked with the startup and shutdown of the cooling towers.
  Balance pipes are used to interconnect water pans of cooling towers.
  The main water supply pipe is a collecting pipe that is two gauges larger than the water return pipe.

## Slide 34
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
Cooling Water System Configuration
  Cooling Water System Overview
  Cooling Tower Configuration and Selection
  Cooling Water Pump Configuration and Selection

## Slide 35: Cooling Tower Heat Exchange Principle
Heat exchanging principle of a mechanical draft cooling tower
  The mechanical draft cooling tower is the main equipment for evaporative cooling of circulating water. Its working principle is that the hot circulating water is sprayed from the cooling tower and then flows to a collecting basin. At the same time, the fan blows air from bottom to top in a reverse direction. Therefore, the water film and cold air on the packing are in wide contact, and mass transfer and heat transfer occur, taking away the heat of the circulating water.
  Mainstream cooling tower brands: Marley, Evapco, BAC.
Notes: Heat dissipation modes of cooling water in the cooling tower: contact heat dissipation and evaporative heat dissipation.
Contact heat dissipation
  When the cooling water meets the air, there are three types of heat transfer depending on the difference between the return water temperature Tw1 and the air temperature Tq1 of the cooling tower:
    When Tw1 > Tq1, the cooling water transfers heat to the air and gets cooled.
    When Tw1 = Tq1, there is no heat transfer between the cooling water and the air, and the cooling water temperature remains unchanged.
    When Tw1 < Tq1, the air transfers heat to the cooling water, and the cooling water temperature increases.
  Therefore, when the ambient temperature is equal to or higher than the cooling water temperature, the contact heat dissipation of the cooling tower fails. At this time, its cooling effect will depend entirely on the evaporative heat dissipation of cooling water. Therefore, the cooling effect will be significantly reduced.

## Slide 36
Notes: Evaporative heat dissipation
  Influence of meteorological factors on evaporative heat dissipation of cooling water: Influence of air temperature: The higher the air temperature (dry bulb temperature), the stronger the evaporative heat dissipation. Influence of air humidity: The lower the relative humidity, the faster the evaporative heat dissipation. On the contrary, high ambient humidity results in poor evaporative heat dissipation. When water vapor in the air saturates, evaporation cannot be performed, and the evaporative heat dissipation is equal to zero.
  Influence of air pressure: the lower the air pressure, the easier the water evaporates. Increasing the ventilation of the cooling tower can effectively reduce the static pressure on the surface of the cooling water and facilitate the evaporative heat dissipation of the cooling water.
  Influence of wind speed: The greater the wind speed, the greater the convection heat transfer coefficient. In addition to closed cooling towers, various open cooling towers require natural or mechanical ventilation.
  To sum up, the cooling process of cooling water in a cooling tower is a process of exchanging heat with the air, and its cooling effect is greatly affected by atmospheric weather conditions.

## Slide 37: Cooling Tower Classification
Classification Basis | Category | Characteristics
Shape | Round tower | Small projects with a flow of less than 100 m3/h and no requirements for water drift and noise, occupying a large area (rarely used)
 | Square tower | Can be assembled, 30% more expensive than the round tower.
Airflow direction | Crossflow tower | Low noise, high cost-effectiveness, and high market share (commonly used)
 | Counterflow tower | Effective and noisy
Material | Stainless steel tower | -
 | Fiberglass tower | Cost-effective (commonly used)
Contact with air? | Open tower | The upfront investment is low, but water refilling is required (commonly used)
 | Closed tower | The cooling capacity is small, and the capital expenditure (CAPEX) is 10 times that of the open tower. However, the subsequent operation cost is low.
Crossflow tower
Counterflow tower
Notes: The water-cooled chilled water unit must use a cooling tower. The air-cooled chiller water unit does not require the cooling tower.

## Slide 38: Cooling Tower Installation Position
The three common positions for installing cooling towers are as follows:
  When the chiller plant is installed in the basement of a building, and the cooling tower is installed on the well-ventilated outdoor green belt or outdoor ground.
  If the chiller plant is a single-storey building, the cooling tower can be installed on the roof of the chiller plant or on the outdoor ground.
  When the chiller plant is installed in the ground floor or basement of a multi-storey building or a high-rise building, the cooling tower is installed on the roof of the podium of the building. If the chiller plant is not installed in the mentioned locations, the cooling tower can only be installed on the roof of the main building of a high-rise building.
Scenario 1
Scenario 2
Scenario 3

## Slide 39: Cooling Tower Selection
Cooling tower flow rate (m3/h)
Chiller working condition (return and supply water temperatures, ℃)
Local outdoor wet bulb temperature (℃)
Location and ventilation
Noise
Floor area
Antifreezing
Final flow rate of the cooling tower
Water quality requirements
Water refilling
Parameters to be considered
Actual factors to be considered
END
Notes: An open cooling tower is recommended for the cooling system of a data center. If water needs to be protected against pollution, a closed cooling tower can also be used. The combustion performance level of cooling tower materials cannot be lower than Class B1.
The cooling tower should not be deployed near heat sources, exhaust gas, smoke generation point, chemical stack, or coal stack.
The distance between cooling towers or between a cooling tower and other buildings should be set based on the ventilation requirements of the tower and the interaction between the tower and the buildings. In addition, the safety distance for fire prevention and explosion prevention of the building and the construction and maintenance requirements of the cooling tower should also be considered
The cooling tower must be far away from high temperature or harmful gas, such as air exhaust from the kitchen. In addition, the cooling tower must be free from water drifting that may affect the surrounding environment.

## Slide 40
Notes: The impact of the cooling tower noise on the environment should comply with the standard values of various urban areas or environmental noise specified in the GB 3096 Environmental Quality Standard for Noise. The space attenuation of the cooling tower can be calculated based on the assumption that the attenuation is 5 dB when the distance increases by one time of the noise value. The synthetic sound pressure level of sound sources of multiple cooling towers should be calculated by logarithm.
After the position of the cooling tower is determined, if the designed and selected low-noise cooling tower cannot meet the requirements, noise reduction and insulation measures should be taken.
Areas with the risk of freezing. The following antifreezing and thermal insulation measures should be taken for a cooling tower running in winter:
  It is recommended that the cooling tower be separately deployed and the antifreeze cooling tower be used.
  The water refill pipes, cooling water supply and return pipes installed on the roof and in the rooms without heating should be insulated and heated. The chassis of the cooling tower for storing water should also be equipped with trace heating facilities.
  For the cooling water pipe installed on the outdoor sunny side, the length of the pipe that is exposed to the sunlight and generates temperature rise can be considered for heat insulation.

## Slide 41: Cooling Tower Water Flow Calculation
Calculate the water flow processed by a cooling tower as follows:
  G = 1.2 * 3600 Q/ (ρ * C * Δt) = 0.86 * 1.2 * Q/Δt
  G: the designed water volume of the cooling tower
  1.2: allowance coefficient
  Q: chiller condensing heat (kW). Q = Chiller cooling capacity + Compressor input power
  ρ: water density at 35℃ (993.96 kg/m3)
  C: specific heat capacity of water at constant pressure (4.1784kJ/kg * K)
  Δt: the temperature difference of the cooling water system (℃)
Notes: When selecting a cooling tower, you can preliminarily select the cooling tower specifications based on the return and supply water temperature, local wet bulb temperature, and cooling tower water flow. Then, you can check whether the selected cooling tower meets the parameter requirements of cooling water based on the curve or table of non-standard working conditions for the sample. If the requirements are not met, the specifications should be modified.

## Slide 42: Cooling Tower Water Refilling
For a system without a water tank, water should be refilled at the bottom of the cooling tower. If a water tank is configured, water should be refilled in the water tank.
The diameter of the cooling water refill pipe should be determined based on the water refill volume qbc. The cooling water refill volume is the sum of the evaporation loss, drainage loss, drift loss, and other losses of the cooling water system. It can be calculated as follows:
  Qbc = qz + qw + qp + qq
  Qbc: cooling water refill volume (m3/h)
  Qz: water loss volume due to evaporation (m3/h)
  Qw: water loss volume due to drainage (m3/h)
  Qp: water loss volume due to drift (m3/h)
  Qq: other lost water volume (m3/h)
Notes: The cooling water refill system must meet the performance requirements of the air conditioning system in a data center. The flow and pressure of the cooling water refill system must meet the requirements of the equipment in use.
If the cooling water refill is interrupted, the cooling system will be interrupted. In this case, a water refill storage device should be deployed. The storage time should not be shorter than the time for a local emergency water truck to arrive at the site. If the storage time cannot be determined, it should be at least 12 hours. A water refill port should be reserved on the water refill storage device.
It is recommended that municipal tap water be used to refill cooling water. Epigenetic water, well water, lake water, and river water that meet the water quality requirements can also be used.
Measures should be taken for the storage of cooling water to prevent the water quality from deteriorating.
Evaporation loss: The evaporation loss of cooling water is related to the cooling water temperature drop. Generally, when the temperature decreases to 5°C, the evaporation loss is 0.93% of the circulating water volume. When the temperature drops to 8°C, it is 1.48% of the circulating water.
Drift loss: water loss due to the strong wind of the cooling tower. The drift loss of China-made equipment is 0.3% to 0.35% of the circulating water volume, and that of international equipment is 0.15% to 0.3% of the circulating water volume.
Drainage loss: The concentration times of cooling water should not exceed 3 to 3.5 times through drainage. Generally, the drainage loss should be 0.3%–1% of the circulating water volume.
Other losses: cooling water losses caused by water leakage.
In conclusion, the general water refill rate can be estimated to be 2% to 3%.

## Slide 43
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
Cooling Water System Configuration
  Cooling Water System Overview
  Cooling Tower Configuration and Selection
  Cooling Water Pump Configuration and Selection

## Slide 44: Flow Lift Calculation for a Cooling Water Circulating Pump
The flow calculation method of a cooling water pump is the same as that of a chilled water pump.
The lift of a circulating water pump should be calculated as follows:
  Take an open cooling tower as an example. The lift calculation formula is as follows:
  H = K * (H1 + H2 + H3 + H4)
  H1: the height difference (m) between the lowest water level of the water pan of the cooling tower and the water distributor or water return (When there is a cooling water tank, H1 indicates the height difference between the lowest water level of the water tank and the water distributor or water return.)
  H2: the hydraulic head (m) required for the water distributor of the cooling tower
  H3: the resistance (m) of the chiller condenser.
  H4: total resistance of the pipe system (m) (including the local resistance of the control valve and dirt remover)
Note: Detailed hydraulic calculation is required.
Notes: The lift of a cooling water pump should be the sum of the following items:
  Height difference between the water pan of the cooling tower and the water distributor.
  Free hydraulic head required by the distributor pipe of the cooling tower: provided by the manufacturer. For details, see the product brochure. Generally, the free hydraulic head of a typical crossflow tower is 0.05 MPa.
  Chiller condenser resistance: provided by the manufacturer. For details, see the product brochure.
  Resistance of suction pipes, discharge pipes, fittings, automatic control valves, filters, and dirt removers.
  Add 5% to 10% of the sum of the preceding items.

## Slide 45: Lift Estimation for a Cooling Water Circulating Pump
The lift design of a cooling water pump is similar to that of a chilled water pump. The main difference is that the height difference between the water pan of the cooling tower and the nozzle needs to be calculated for an open system.
Cooling water pump lift components (can be used for drawing or equipment reviewing)
  Water resistance of the chiller condenser: generally 5 to 7 mH2O (For details, see the product sample.)
  Water spray pressure of the cooling tower nozzle: generally 2 to 3 mH2O
  Height difference between the water pan and the nozzle of the cooling tower (open cooling tower): generally 2 to 3 mH2O
  Return water filter resistance: generally 3 to 5 mH2O
  Loss due to water pipe friction resistance and local resistance loss of the cooling system: generally 5 to 8 mH2O
To sum up, the lift of the cooling water pump ranges from 17 mH2O to 26 mH2O. Generally, the lift ranges from 21 mH2O to 25 mH2O.
Note: The lift must be calculated based on the actual situation of the cooling system. Do not copy the empirical value.
Condenser
Cooling water nozzle
Height
difference
Filter

## Slide 46
Chilled Water Air Conditioner Design Overview
Chilled Water System Configuration
Cooling Water System Configuration

## Slide 48
Shenjutao/WX352174
2020.10.01
Lishaofeng/00486775
New