## Slide 1: Energy-Saving Solution Configuration for Data Center Cooling Systems

## Slide 2
This course describes how to configure energy-saving solutions for air conditioning systems in data centers and how to improve the reliability of air conditioning systems in data centers by means of continuous cooling.

## Slide 3
On completion of this course, you will be able to:
  Master the method of configuring air conditioning systems for free cooling in data centers.
  Master the method of configuring continuous cooling for air conditioning systems in data centers.

## Slide 4
Free Cooling Solution Configuration for Data Center Air Conditioners
  Direct Ventilation Free Cooling Solution Configuration
  Water-based Free Cooling Solution Configuration
  Indirect Evaporative Cooling Solution Configuration
Continuous Cooling Solution Configuration for Data Center Air Conditioners
Configuration Cases for Data Center Air Conditioning Systems

## Slide 5: Concept of Direct Ventilation Free Cooling
In the season when the ambient temperature is low, outdoor air is directly introduced to a data center as a cooling source after being filtered and humidified, which saves a large amount of energy. This cooling mode is called air-cooled free cooling or direct ventilation free cooling. This solution features simple working principles and low costs, and can reduce energy consumption of data centers.
CRAC
40°C
30°C
20°C
35°C
20°C
5°C

## Slide 6: Working Principle of Direct Ventilation Free Cooling
Outdoor temperature ≤ 5°C
20°C < Outdoor temperature ≤ 25°C
5°C < Outdoor temperature ≤ 20°C
Outdoor temperature > 25°C
CRAC
30℃
20℃
5℃
CRAC
30℃
20℃
20℃
CRAC
20℃
25℃
30℃
CRAC
20℃
40℃
30℃
Notes: When the outdoor air condition is within the specified range (generally lower than 20°C), outdoor cool air is filtered by the filter using fans and louvers, and then is directly sent to a data center. In direct ventilation mode, the compressor of the air conditioner stops working. The fans exchange the outdoor cold air with the indoor hot air. Therefore, the energy consumption of the air conditioner is extremely low. In theory, the energy efficiency ratio (EER) of the air conditioner can reach 25, and the dynamic power usage effectiveness (PUE) can be as low as 1.10.
When the outdoor temperature is higher than the air intake temperature of the device, the direct ventilation device automatically shuts down and the air conditioner starts for cooling. In electric cooling mode (non-direct ventilation), the EER of the air conditioner depends on the efficiency of the air conditioner. Generally, the EER ranges from 3 to 6, and the dynamic PUE is 1.39. The annual average PUE depends on the energy efficiency in electric cooling mode and the running time in direct ventilation mode (that is, the local climate).

## Slide 7: Composition of a Direct Ventilation Free Cooling System
Direct ventilation free cooling system diagram
Notes: A filter is to filter the outdoor fresh air to meet the cleanliness requirements of the indoor environment. Filters can be classified into roughing filters and medium efficiency filters.
Humidifiers used in data centers include dry steam humidifiers, infrared humidifiers, spray humidifiers, high-pressure atomizing humidifiers, air water mixed humidifiers, ultrasonic humidifiers, and wet film humidifiers. The most common humidifiers used in data centers are electrode humidifiers, infrared humidifiers, wet film humidifiers, and ultrasonic humidifiers. Electrode humidifiers and infrared humidifiers are widely used in the humidification systems of precision air conditioners. Wet film humidifiers are the most widely used independent humidifiers in data centers and are referred to as "data center humidifiers".

## Slide 8: Three Configuration Solutions for Direct Ventilation Free Cooling
The cooling system of the direct ventilation free cooling solution supports direct ventilation cooling and mechanical cooling. Mechanical cooling is enabled only when the outdoor temperature cannot reach the preset temperature.
There are three mechanical cooling modes that can work with free cooling: water-cooled chilled water, air-cooled chilled water, and air cooling.
Mode 3: air-cooled air conditioner
Mode 2: air-cooled chilled water air conditioner
Mode 1: water-cooled chilled water air conditioner
Free cooling
source
Air
conditioner
outdoor unit
Air blender
Air
conditioner
indoor unit
Auxiliary evaporator
(optional)
Air filter
Air intake
vent/Fan
Air exhaust
vent
Dry cooler +
Chiller
Cooling tower
Air
conditioner
indoor unit
Chiller
Air
conditioner
indoor unit
Independent humidifier
(optional)
Mechanical cooling
IT device

## Slide 9: Application Scenarios of Direct Ventilation Free Cooling
Direct ventilation is susceptible to the external environment. Therefore, site selection is critical to a data center using direct ventilation. A site must be selected from the following two aspects:
  Climate. More energy is saved in a region with a higher latitude or lower temperature.
  Air quality. The solution feasibility depends on the air pollution degree. A site should be located in a region with low pollution to prevent the indoor equipment from being corroded.
According to the preceding analysis and suggestions of direct ventilation vendors, the direct ventilation solution is not recommended if the annual average temperature outside a data center is above 20°C.
If the outdoor air quality is poor, the direct ventilation solution is not recommended. Chemical filters are not recommended for data centers due to their large air resistance, heavy maintenance workload, and high cost. Therefore, during outdoor environment evaluation, the direct ventilation solution is not recommended for areas with poor air quality. For details about the standards for outdoor harmful gas concentration, see ASHRAE 66.1. The following table lists the requirements.
Contaminant | Major Standards | Average Time
Carbon monoxide | 9 ppm (10 mg/m3) | 8-hour
 | 35 ppm (40 mg/m3) | 1-hour
Lead | 1.5 μg/m3 | Quarterly average
Nitrogen dioxide | 100 μg/m3 | Annual arithmetic average
PM10 | 150 μg/m3 | 24-hour
PM2.5 | 35 μg/m3 | 24-hour
Ozone | 0.08 ppm | 8-hour
Sulfur oxides | 0.14 ppm | 24-hour
Equator
Arctic Circle
Distribution of annual mean temperature around the globe
Antarctic Circle
Tropic of Cancer
Tropic of
Capricorn
Notes: Take STULZ as an example. In the design process, the direct ventilation solution is determined by querying the annual ambient temperature of the place where the data center is located and calculating the number of days/hours when the annual ambient temperature is lower than the preset supply air temperature. Set the supply air temperature to 24°C for 8760 hours in a year. If the ambient temperature is lower than 24°C for more than half of the time, direct ventilation can be used for cooling.

## Slide 10: Flowchart for Configuring a Direct Ventilation Free Cooling System
Requirement specifications input
Supply and return air status design
Cooling load calculation
Mechanical cooling design and selection
Selection of the functional section of the direct ventilation device
Fan design and selection
Cleanliness design and selection
Humidity design and selection
Air vent design and selection
Control system design
Material list output
Note: The design of air supply fans, cleanliness, and humidity is integrated in the direct ventilation device. When selecting a direct ventilation device, you need to determine the three specifications.
Notes: The yellow parts are the key parts described in this slide. Other parts are described in other sections.
Requirement specifications input: cabinet power density, cabinet quantity, data center area, and data center environment specifications (dry-bulb temperature, relative humidity, pParticulate matter concentration, and harmful gas concentration)
Supply and return air status design: Determine the supply and return air status (supply and return air temperature and humidity) of the data center. If the preset supply and return air temperatures are higher, the free cooling time using the outdoor air is longer, and the time for starting the compressor is shorter, which reduces the power load of the compressor.
Cooling load calculation: Calculate the cooling load of the data center.

## Slide 11
Notes: Mechanical cooling design and selection: Select a cooling solution, design and select the chiller based on the load, and calculate the air volume of the unit. The design of mechanical cooling is to determine the auxiliary cooling mode. A high-efficiency mechanical cooling mode can reduce the cooling loss and the cooling power load.
Fan design and selection: exhaust fan design (air volume and motor power)
Selection of the functional section of the direct ventilation device: Select a functional section (cooling, humidification, filtering, or preheating). Design air blender dimensions.
Cleanliness design and selection: Determine the filtering mode, level, and cross-sectional area.
Humidity design and selection: Output the humidification mode and humidification capacity. If the preset humidity range is wider, the time required for humidifying a data center is shorter, and the humidification capacity is less, which reduces the energy consumption caused by humidification.
Air vent design and selection: 1. Determine the types of required air vents (anti-freezing air vent, return air vent, exhaust air vent, and
Control system design: Complete the control logic design.
Material list output: Output the general material list based on the preceding material selection solution.

## Slide 12: Specifications Input and Supply and Return Air Status Design
Specifications input
Supply and return air status design
  Preset anti-freezing temperature (Tf)
  Supply air temperature (Ts±Δt) (considering
  the air conditioner control precision)
  Designed return air temperature (Tr)
  Supply air humidity range (RHl, RHh)
Input specifications 1: customer requirement specifications | 
Cabinet power density | 
Number of cabinets | 
Data center area | 
Input specifications 2: outdoor specifications | 
Annual environmental specifications of the data center | Temperature (dry-bulb temperature)
 | Humidity (relative humidity or humidity ratio)
 | Particulate matter concentration
 | Harmful gas concentration
 | Local wind direction
Ambient temperature requirements for data center devices
Based on indoor specifications requirements
Notes: Anti-freezing temperature: If the outdoor temperature is below 3°C, open the anti-freezing air damper to preheat the outdoor air.
If the preset supply and return air temperatures are higher, the free cooling time using the outdoor air is longer, and the time for starting the compressor is shorter, which reduces the power load of the compressor.
If the preset humidity range is wider, the time required for humidifying a data center is shorter, and the humidification capacity is less, which reduces the energy consumption caused by humidification.
Particulate matter concentration involves filter selection. Generally, the information about the concentration of outdoor particulate matter and the filtering level that the data center needs to meet are submitted to the filter vendor.
The harmful gas concentration determines whether a chemical filter should be configured. Chemical filters do not meet the requirements for low PUE due to large air resistance, heavy maintenance workload, and high cost.
Data center air supply and return status design is based on the ambient temperature requirements of the data center equipment and the customer's requirements. In principle, if the preset supply and return air temperatures are higher, the free cooling time using the outdoor air is longer, and the time of auxiliary mechanical cooling is shorter, which reduces the cooling load of the data center.

## Slide 13: Mechanical Cooling Design and Selection
Key points for mechanical cooling selection
  When selecting the direct expansion (DX) or chilled water cooling solution, consider whether the customer allows water to enter the equipment room, whether the outdoor unit is installed more than 30 m away from the indoor unit, and whether the building has an existing chilled water system.
  If the building already has a chilled water system and the customer allows water to enter the equipment room, the chilled water system is recommended because it has high energy efficiency and the power load is less than that of the DX system.
  After determining the auxiliary cooling solution, you need to optimize the selection of components involved in the cooling solution.
  The water-cooled chilled water solution is used in the preceding scenarios.
Chilled water cooling solution
DX cooling solution
Note: For details about mechanical cooling selection, see Load Calculation and Air Conditioner Configuration for Data Center Cooling System and Data Center Chilled Water Air Conditioning System Configuration.
Server room
Direct ventilation air conditioner
Chilled water
Refrigerant
Chiller
Expansion valve
Compressor
Evaporator
Other indoor
units
Condenser
CRAC
40℃
30℃
20℃
35℃
20℃
5℃
Notes: According to TIA 942 requirements, it is recommended that different redundancy modes be used for components in mechanical cooling for data centers of different tiers, as shown by the following:
  (1) Tier 1 data centers: Components are not redundant.
  (2) Tier 2 and Tier 3 data centers: Components (such as indoor air conditioners, outdoor cooling water pumps, chilled water pumps, and chillers) work in N+1 redundancy mode.
  (3) Tier 4 data centers: Components (such as indoor air conditioners, outdoor cooling water pumps, chilled water pumps, and chillers) work in N+X redundancy mode.

## Slide 14: Humidity Control of Direct Ventilation Equipment and Selection of Air Blenders
Humidity control
  In the direct ventilation solution, electrode humidifiers and high-pressure micro-mist humidifiers are recommended.
Selection of air blenders
  Selection of functional sections
  Cold air processing involves filtering, humidification, preheating, cooling, and dehumidification. Corresponding functional sections need to be designed for these processes.
  Dimensions design
  An air blender is used to filter and humidify the introduced outdoor fresh air. When designing air blender dimensions, consider the following two situations:
  Only the intake air damper and return air damper are available. The anti-freezing air damper is not considered.
  The intake air damper, return air damper, and anti-freezing air damper are available.
  In addition to different types of air dampers, the specifications of the filtering section and humidification section need to be considered based on the actual project requirements.
Fresh air vent
Primary filter
Chemical filter
Compressor
Evaporator
Micro-mist humidifier
Air supply fan
Medium efficiency filter
Air return vent
Air supply vent
Functional sections of a direct ventilation air conditioning system

## Slide 15: Selection of Direct Ventilation Air Supply Fans and Exhaust Fans
The air supply fan is inside the direct ventilation device, and the exhaust fan is outside the direct ventilation device.
Selection of air supply fans
  Air supply volume calculation
  Q: heat load (kW) of the data center
  ρ: air density. The recommended value is 1.2 kg/m3.
  cp: specific heat of the air at constant pressure. The recommended value is 1.01 kJ/kg·°C.
  t1 and t2: preset room temperature and outdoor supply air temperature (°C)
  K1: margin coefficient for calculating the supply air volume. Generally, the value ranges from 1.1 to 1.2.
Calculation of supply air pressure
  Pfan > ΔPm + ΔPj + Pfiltering + Phumidification
Design and selection of exhaust fans
  The number of exhaust fans is equal to the number of precision air conditioners determined during the mechanical cooling design.
  The air volume of the exhaust fan is approximately the same as that of the selected air supply fan.
Name | Specifications
Axial fan (exhaust fan) | Dimensions (R x W): 720 mm x 460 mm; rotation speed: 1450 rpm; blade angle: 25 deg; air volume: 15,297 m3/h; air pressure: 224 Pa; power = 1.5 kW
Notes: The total pressure of the fan is mainly used to overcome the resistance encountered in the air supply process. Take the air supply fan as an example. The resistance of the fan includes the friction drag, local resistance, and resistance of functional sections (filtering and humidification sections).
The friction drag (ΔPm) is related to the pipe material and pipe length: ΔPm = Δpm x l.
Local resistance is mainly caused by the change of air flow direction. When a vortex occurs in the air that flows through a cross section, local resistance is generated. Formula for calculating the local resistance: ΔPj = ζ x ρ x v²/2. In the formula, ζ indicates the local resistance coefficient, and V indicates the air flow rate at the place where the local pressure loss occurs in the air duct.

## Slide 16: Filter Selection for Direct Ventilation Devices
Filter selection
Filter class
  In the actual engineering design, according to the data center air cleanliness requirements specified in the ASHRAE, primary filters and medium efficiency filters are generally used for air ducts. G4 primary filters and F7 medium efficiency filters are usually selected in the industry to ensure good filtering effects. G4 primary filters are recommended for the return air section.
Calculation of filter cross-sectional area
  Q: air supply volume (m3/h) through the filter
  U: windward speed (m/s) of the cross section of the filter. In the industry, the value of 1.87 m/s to 3.73 m/s is usually used.
  F: cross-sectional area (m2) of the filter
Particulate matter contamination | The cleanliness of a data center must meet the ISO 14644-1 (ISO 1999) class 8 requirements. A proper filter is required to meet the cleanliness requirements of this class. 1. MERV 8 filters recommended by ASHRAE Standard 127 (2007a) should be used to filter room air. 2. MERV 11 or MERV 13 filters recommended by ASHRAE 2009b should be used to filter the outdoor air entering a data center.
Requirements for particulate matter concentration in data centers
Filter standards for data centers recommended by ASHRAE
Recommended fresh air filter:
MERV 11–13 filter
Recommended return air filter:
MERV 8 filter
CRAC
30℃
20℃
5℃
Indoor dust requirements:
ISO 14644-1 Class 8

## Slide 17: Direct Ventilation Control Logic Design
Control logic design
  Cooling mode design principle: The cooling mode is automatically selected by the air conditioner controller based on the outdoor ambient temperature and the actual load of the indoor equipment room. The switching logic of the cooling mode is controlled by three key temperatures: preset anti-freezing temperature (Tf), supply air temperature (Ts), and designed return air temperature (Tr).
  Considering the control precision of the air conditioner, the supply air temperature range of the air conditioner is set to Ts±Δt. The following table describes cooling mode switching based on the outdoor ambient temperature.
No. | Environment Requirement | Cooling Mode
1 | Tf ≤ t < Ts – Δt°C | Direct ventilation cooling (fresh air + return air mixture)
2 | t < Tf°C | Direct ventilation cooling (fresh air + anti-freezing air mixture)
3 | Ts – Δt < t ≤ Ts + Δt°C | Direct ventilation cooling (all fresh air)
4 | Ts + Δt ≤ t < Tr°C | Direct ventilation + mechanical cooling (hybrid operating mode)
5 | t ≥ Tr°C | Complete mechanical cooling (chilled water or DX cooling)
Operating Mode | Intake Air Damper | Return Air Damper | Anti-freezing Air Damper | Exhaust Air Damper
Chilled water/DX mechanical cooling | 0% | 100% | 0% | 0%
Hybrid cooling | 100% | 0% | 0% | 100%
Direct ventilation cooling | 100% | 0% | 0% | 100%
Direct ventilation cooling① | 0–100% | 0–100% | 0% | 0–100%
Direct ventilation cooling② | 0–100% | 0–100% | 100% | 0–100%
Operating mode and indoor air damper linkage control status
Cooling mode
Notes: Tf ≤ t < Ts – Δt°C: Direct ventilation is used for cooling. To ensure the supply air temperature, the return air damper is open to increase the air temperature by mixing air. In this mode, the fresh air damper, return air damper, and exhaust air damper are open, the anti-freezing air damper is completely closed, and the compressor stops running.
t < Tf°C: Direct ventilation is used for cooling. To prevent the introduced outdoor air from being too cold, open the anti-freezing air damper to preheat the outdoor air and increase the supply air temperature. In this mode, the anti-freezing air damper is 100% open, the opening angles of the supply air damper, exhaust air damper, and return air damper are controlled, and the compressor stops running.
Ts – Δt < t ≤ Ts + Δt: Direct ventilation is used for cooling, and the compressor stops running. In this mode, the fresh air damper and exhaust air damper are open, and the anti-freezing air damper and return air damper are completely closed.
Ts + Δt ≤ t < Tr: Direct ventilation and mechanical cooling are used for hybrid cooling. In this case, the outdoor air temperature is lower than the return air temperature of the equipment room. If the compressor is used for hybrid cooling, the energy consumption is lower than that when only the compressor is used for cooling. In this mode, the supply air damper and exhaust air damper are open, and the return air damper and anti-freezing air damper are completely closed.
t ≥ Tr: The compressor is used for cooling. In this case, energy consumption of the compressor is the highest. In this mode, the supply air damper, return air damper, and anti-freezing air damper are completely closed, and the exhaust air damper is open.

## Slide 18
Free Cooling Solution Configuration for Data Center Air Conditioners
  Direct Ventilation Free Cooling Solution Configuration
  Water-based Free Cooling Solution Configuration
  Indirect Evaporative Cooling Solution Configuration
Continuous Cooling Solution Configuration for Data Center Air Conditioners
Configuration Cases for Data Center Air Conditioning Systems

## Slide 19: Water-based Free Cooling Solution Overview
The heat exchanger acts as the bypass mode of the water chiller. When the outdoor air condition is within the configured range, the chilled water in the data center is cooled by using the cooling water. The pump sends the cooling water through the plate heat exchanger to cool the chilled water in the CRAH without mixing the cooling water and chilled water. The bypass valve of the chiller can be closed based on the condensate water temperature. This type of energy-saving cooling mode supports free cooling for some loads when the heat exchanger and the chiller are connected in series.

## Slide 20: Composition of a Water-based Free Cooling System
In mode 1, the main components include the cooling tower, chiller, water-to-water heat exchanger, water pump, and indoor unit of the in-room or in-row chilled water air conditioner.
In mode 2, the main components include the integrated air-cooled chiller with the free cooling function, water pump, and indoor unit of the in-room or in-row chilled water air conditioner.
Mode 1: water-cooled chilled water + indirect free cooling
Mode 2: air-cooled chilled water + indirect free cooling
Integrated dry cooler
Air-cooled chiller
Data Center
Pump
Notes: The water-cooled chilled water free cooling system consists of the chiller, plate heat exchanger, cooling tower, water pump, thermal storage tank, and other auxiliary components (water pipes and meters).
  The chiller is mainly used for mechanical cooling.
  The plate heat exchanger is used to directly exchange heat between the cooling water and chilled water.
  The cooling tower is used to cool the cooling water.
  The water pump is used to provide power for the whole water-cooled liquid.
  The thermal storage tank is used to cool the data center when the power supply is disconnected.
The air-cooled chilled water free cooling system consists of the air-cooled chiller, water pump, thermal storage tank, and other auxiliary components (water pipes and meters). The coil pipe for free cooling is integrated with the outdoor unit. The functions of other components are the same as those of the water-cooled chilled water system.

## Slide 21: Water-based Free Cooling System Configuration Process
Requirement specifications input
Determination of the specifications of air supply and return as well as water supply and return
Cooling load calculation
System mode selection
Main device selection
Main device and indoor unit layout
Pipe layout of the water system
Water system calculation
Other device selection
Output of HVAC system solution drawings and material lists
Notes: The yellow parts indicate the key points described in this slide for water-based free cooling system configuration and selection.
Requirement specifications input: cabinet power density, cabinet quantity, data center area, whether free cooling is required, and reliability level
System mode selection: 1. Output the chilled water system mode: air-cooled free cooling or water-cooled free cooling. 2. Output the subsystem mode. 3. Output the system diagram.
Main device selection: 1. Cooling source device selection 2. Indoor unit selection
Pipe layout of the water system: Output the air conditioner connection diagram.
Water system calculation: Calculate the flow rate and pipe diameter of the chilled water system, cooling water system, and condensate water system.
Other device selection: thermal storage tanks and auxiliary devices

## Slide 22: Key Points of Water-based Free Cooling System Configuration (1)
Design points
Design of air supply and return as well as water supply and return
  Determine the air supply and return specifications of the indoor unit
  Determine the supply and return chilled water temperatures on the cooling source side.
  Supply and return water temperatures of cooling towers: supply and return water in summer and winter
  Supply and return water temperatures on the primary and secondary sides of the plate heat exchanger
 |  | Description
Determine the free cooling type. |  | Direct free cooling/Indirect free cooling
Determine the plate heat exchanger based on the outdoor unit. |  | Water-to-water plate heat exchanger/Air-cooled chiller with the free cooling function
Determine the medium. |  | Water/Glycol
Heat exchanger configuration | Inlet and outlet water temperatures on the primary and secondary sides | Inlet and outlet water temperatures on the primary side: 7°C for inlet water and 12°C for outlet water Inlet and outlet water temperatures on the secondary side: 10°C for inlet water and 5°C for outlet water
 | Material | Alloy 304/Alloy 316
 | Total heat transfer capacity | 900 kW
 | Pressure drop | 10 m
Notes: In summer, the cooling tower is selected for water supply and return. The cooling tower is selected under the most unfavorable working conditions. The supply and return water temperatures in winter are determined when the control logic is designed, which are usually lower than the temperatures of the supply and return cooling water in summer.
The operating mechanism of the air-cooled free cooling system is as follows: When the temperature of the cooling system is within the independent operating temperature range (the ambient temperature is higher than the return water temperature), the fan speed is adjusted based on the condensing pressure to ensure system reliability. When the cooling system and free cooling system are running at the same time (the ambient temperature is lower than the return water temperature but the outlet water temperature is higher than the preset value), the fan runs at full speed. The proportional three-way valve is fully opened to maximize the cooling capacity of the free cooling system. The compressor is started or shut down based on the outlet water temperature. In the temperature range where the free cooling system runs independently (the ambient temperature is lower than the return water temperature and the outlet water temperature is lower than the preset value), the fan speed is adjusted based on the outlet water temperature. The proportional three-way valve performs stepless adjustment based on the outlet water temperature to ensure that the free cooling system is fully utilized and the precision requirements of water temperature control are met.

## Slide 23: Key Points of Water-based Free Cooling System Configuration (2)
System mode selection
  Determine whether to choose the air or water-cooled mode based on the following: 1. Whether the water source is sufficient 2. Whether the installation space meets the water cooling requirements 3. Cooling load
Air-cooled chilled
water free cooling
Water-cooled chilled
water free cooling
Note: For details about how to select a chilled water air conditioner system, see Data Center Chilled Water Air Conditioning System Configuration.
Condenser fan
Free cooling coil pipe
Air-cooled condenser
Expansion valve
Compressor
Evaporator
Three-way valve
Data center
Free cooling heat exchanger
Cooling tower
Water-cooled condenser
Expansion valve
Compressor
Evaporator
Three-way valve
Notes: In summer, the cooling tower is selected for water supply and return. The cooling tower is selected under the most unfavorable working conditions. The supply and return water temperatures in winter are determined when the control logic is designed, which are usually lower than the temperatures of the supply and return cooling water in summer.
The operating mechanism of the air-cooled free cooling system is as follows: When the temperature of the cooling system is within the independent operating temperature range (the ambient temperature is higher than the return water temperature), the fan speed is adjusted based on the condensing pressure to ensure system reliability. When the cooling system and free cooling system are running at the same time (the ambient temperature is lower than the return water temperature but the outlet water temperature is higher than the preset value), the fan runs at full speed. The proportional three-way valve is fully opened to maximize the cooling capacity of the free cooling system. The compressor is started or shut down based on the outlet water temperature. In the temperature range where the free cooling system runs independently (the ambient temperature is lower than the return water temperature and the outlet water temperature is lower than the preset value), the fan speed is adjusted based on the outlet water temperature. The proportional three-way valve performs stepless adjustment based on the outlet water temperature to ensure that the free cooling system is fully utilized and the precision requirements of water temperature control are met.

## Slide 24
Notes: The water-cooled chilled water air conditioning system has the following three operating modes:
(1) In summer, the cooling is completely performed by the chiller, and the plate heat exchanger does not work due to valve regulation.
(2) In winter, only free cooling is adopted. The chiller is shut down and the chilled water and cooling water only pass through the plate heat exchanger by valve regulation.
(3) Free cooling is partially adopted in spring and autumn. In this case, the cooling water and chilled water first pass through the plate heat exchanger and then the chiller. The resistance is higher, and the lift of the water pump should be larger during design (here the cooling water is glycol). Generally, the lift is 1.2 times of the original designed lift. (If water is used as the medium of cooling water, the lift remains unchanged.)

## Slide 25: Key Points of Water-based Free Cooling System Configuration (3)
Main device selection
  The water-to-water plate heat exchanger is a device used for free cooling in the chilled water system. The number of plate heat exchangers is the same as the number of outdoor chillers of the chilled water system that require indirect free cooling. At present, more than 90% of the heat exchangers in the market are plate heat exchangers, because the plate heat exchanger has the highest heat exchange efficiency among all types of heat exchangers.
1. Fixed clamping plate
2. Connection port
3. Gasket
4. Plate
5. Adjustable clamping plate
6. Lower guide rod
7. Upper guide rod
8. Compression bolt
9. Pillar
Five specifications are determined for selecting plate heat exchangers:
(1) Inlet and outlet water temperatures on the chilled water side: for example, 7–12°C.
(2) Inlet and outlet water temperatures on the cooling water side: for example, 5–10°C.
(3) Total heat transfer capacity: approximately equal to the cooling capacity of the chiller; usually multiplied by 1.1
(4) Medium: water/glycol (concentration). The concentration can be obtained by querying the table.
(5) Pressure drop: The lift of a data center ranges from 8 m to 10 m. A larger lift indicates the lower cost of a plate heat exchanger.
Notes: For details about how to select other devices, see Data Center Chilled Water Air Conditioning System Configuration.
In a water-cooled chilled water system, although the water quality on the chilled water side is good, the water quality on the cooling water side is usually poor because the cooling water side is connected to the cooling tower. If a brazed plate heat exchanger is used, dirt in water will be accumulated on the heat exchanger after a period of time. In addition, a brazed plate heat exchanger is not easy to maintain, resulting in a significant decrease in the overall heat exchange efficiency. Therefore, it is recommended that detachable plate heat exchangers be used in water-cooled chilled water systems.
On the contrary, in an air-cooled chilled water system, one side of the system is chilled water, and the other side is air. Therefore, the medium in this case has relatively high cleanliness, and using a brazed plate heat exchanger can effectively improve overall heat exchange efficiency.

## Slide 26
Free Cooling Solution Configuration for Data Center Air Conditioners
  Direct Ventilation Free Cooling Solution Configuration
  Water-based Free Cooling Solution Configuration
  Indirect Evaporative Cooling Solution Configuration
Continuous Cooling Solution Configuration for Data Center Air Conditioners
Configuration Cases for Data Center Air Conditioning Systems

## Slide 27: Operating Principle of Indirect Evaporative Cooling (1)
The air to be processed is cooled by a non-contact air-to-air heat exchanger to obtain air with a reduced temperature and unchanged moisture content. This is a process of cooling air without changing the humidity.
During evaporation, water absorbs heat from the air, which lowers the air temperature. Evaporative cooling is an isenthalpic process of humidifying and cooling air.
③ Secondary air inlet
T3
T4
Primary air is air that is indirectly cooled.
Secondary air is air cooled by direct evaporation.
②: indirect cooling without changing the humidity
③ ④: isenthalpic humidification, direct evaporative cooling process
If 1 g water is added to each kg of air, the air temperature decreases by 2.5°C after the water evaporates.
③
④
①
②
T3
T4
T1
T2
Representation of the indirect evaporative cooling process on a psychrometric chart
Secondary air outlet
Water spraying
Primary air outlet
Primary air inlet
Notes: Heat dissipation modes of cooling water in the cooling tower include contact heat dissipation and evaporative heat dissipation.
Contact heat dissipation
  When the cooling water meets the air, there are three types of heat transfer depending on the difference between the inlet water temperature Tw1 and the air temperature Tq1 of the cooling tower:
    When Tw1 is greater than Tq1, the cooling water transfers heat to the air and gets cooled.
    When Tw1 is equal to Tq1, there is no heat transfer between the cooling water and the air, and the cooling water temperature remains unchanged.
    When Tw1 is less than Tq1, the air transfers heat to the cooling water, and the cooling water temperature increases.
  Therefore, when the ambient temperature is equal to or higher than the cooling water temperature, the contact heat dissipation of the cooling tower fails. At this time, its cooling effect will depend entirely on the evaporative heat dissipation of the cooling water. Therefore, the cooling effect will be significantly reduced.

## Slide 28
Notes: Evaporative heat dissipation
  Influence of meteorological factors on evaporative heat dissipation of cooling water: Influence of air temperature: The higher the air temperature (dry-bulb temperature), the stronger the evaporative heat dissipation. Influence of air humidity: The lower the relative humidity, the faster the evaporative heat dissipation. On the contrary, high ambient humidity results in poor evaporative heat dissipation. When water vapor in the air saturates, evaporation cannot be performed, and the evaporative heat dissipation capacity is equal to zero.
  Influence of air pressure: The lower the air pressure, the easier the water evaporates. Increasing the ventilation of the cooling tower can effectively reduce the static pressure on the surface of the cooling water and facilitate the evaporative heat dissipation of the cooling water.
  Influence of wind speed: The greater the wind speed, the greater the convection heat transfer coefficient. In addition to closed cooling towers, various open cooling towers require natural or mechanical ventilation.
  To sum up, the cooling process of cooling water in a cooling tower is a process of exchanging heat with the air, and its cooling effect is greatly affected by atmospheric weather conditions.

## Slide 29: Operating Principle of Indirect Evaporative Cooling (2)
Uses an air-to-air heat exchanger to lower the indoor temperature through the outdoor low-temperature cooling source.
Fully utilizes the difference between dry- and wet-bulb temperatures to prolong the free cooling time by using a spray system.
Starts mechanical cooling for auxiliary cooling when the cooling capacity provided by free cooling is insufficient.
Outdoor
fresh air
Indoor air
return
Indoor air
supply
Outdoor air
exhaust
Metal plate heat exchanger
Polymer tube heat exchanger
Outdoor air
exhaust
Indoor air supply
Indoor air supply
Outdoor
fresh air
Indoor air
return
Outdoor
fresh air
Notes: The water-cooled chiller must use a cooling tower. The air-cooled chiller does not require a cooling tower.

## Slide 30: Operating Mode of Huawei Indirect Evaporative Cooling Devices
Dry mode (only the fan started)
Wet mode (fan and water pump started)
Hybrid mode (fan, water pump, and compressor started)
Different cooling components are started based on the outdoor fresh air.
Indoor return air
Outdoor fresh air
Outdoor air exhaust
Supply air to the data center
Operating Mode | Outdoor Ambient Temperature (100% Load) | Fan | Water Pump | Compressor
Dry mode | Dry-bulb temperature ≤ 16°C | ON | OFF | OFF
Wet mode | Dry-bulb temperature > 16°C, wet-bulb temperature ≤ 19°C | ON | ON | OFF
Hybrid mode | 19°C < Wet-bulb temperature ≤ 34°C | ON | ON | ON
Outdoor air exhaust
Data center supply air temperature: 24°C
Outdoor dry-bulb temperature ≤ 16°C (only the fan started)
Data center return air temperature: 36°C
Outdoor fresh air
Outdoor air exhaust
Data center supply air temperature: 24°C
Data center return air temperature: 36°C
Outdoor fresh air
Outdoor air exhaust
Data center supply air temperature: 24°C
20°C ≤ Outdoor wet-bulb temperature ≤ 32°C (fan, water pump, and compressor started)
Data center return air temperature: 36°C
Outdoor fresh air
Wet bulb
Wet bulb
Notes: Dry mode: When the dry-bulb temperature of the outdoor air is lower than a critical value, only the outdoor low-temperature air can be used to cool the thermal circulation air in the data center through an air-to-air heat exchanger.
Wet mode: When the dry-bulb temperature of the outdoor air is higher than the critical value of the dry mode but the wet-bulb temperature is lower than a certain critical value, the evaporative cooling principle can be used to perform isenthalpic humidification and cooling on the outdoor air and then the thermal circulation air in the data center can be cooled through an air-to-air heat exchanger.
Hybrid mode: When the wet-bulb temperature of the outdoor air is higher than the critical value of the wet mode, the evaporative cooling principle can be used to perform isenthalpic humidification and cooling on the outdoor air and then the thermal circulation air in the data center can be cooled through an air-to-air heat exchanger. At the same time, parts with insufficient cooling capacity are supplemented by the backup DX or chilled water mechanical cooling system.
The critical temperature value generally depends on the structure, material, adiabatic evaporation mode, and heat exchange efficiency of a heat exchanger.

## Slide 31: Indirect Evaporative Cooling System Composition
The typical structure of an indirect evaporative cooling air conditioner is used as an example.
Air conditioner shell
Fan on the secondary side
Air flow on the secondary side
Air flow on the primary side
Air-to-air heat exchanger
Surface cooler coil
Fan on the primary side
Air filter on the primary side
Air filter on the secondary side
Automatic shutdown air damper
Adiabatic evaporative cooling and humidification device
Notes: Generally, an indirect evaporative cooling air conditioner consists of an air-to-air indirect heat exchanger, an adiabatic evaporative cooling device, fans on the primary and secondary sides, air filters, an air damper, and a backup mechanical cooling cycle.
Main structures of air conditioners can be different, depending on the vendors' design.
Air-to-air heat exchangers may have different structures and materials, but they are generally cross-air flow heat exchangers. The heat exchange efficiency of different heat exchanger types is different.
The air inlet and outlet directions on the secondary side can be parallel and reverse to those on the primary side, as shown in the figure. They can also be vertical and cross-connected, depending on the design structure of the air conditioner.
The evaporative cooling and humidification can use the adiabatic spray (or micro-mist) mode or a mode similar to the cooling tower operating principle. Water is directly sprayed on an air-to-air heat exchanger, which leads to higher heat transfer efficiency in wet working conditions than dry working conditions.
A water treatment system and water circulation pump system are usually used together with an evaporative cooling system.
The backup mechanical cooling cycle can be a DX compressor cooling cycle or a chilled water surface cooler coil type, depending on the design and actual application conditions of the air conditioner.

## Slide 32: Application Scenarios of Indirect Evaporative Cooling
The indirect evaporative cooling solution applies to the following scenarios:
  Climatic environment: applicable to areas where the ambient temperature is low or the temperature is high and the humidity is low. The optimal average temperature is below 20°C.
  Altitude: ≤ 1000 m (> 1000 m: requires derating design)
  Geographical environment: abundant water resources and cheap water price
  Typical regions: Europe, Central Asia, Russia, North China, and Northwest China
  Outdoor installation design, large installation space needed for the large equipment, and suitable for newly-built buildings (equipment and building planned together)
  Various air supply and return modes
  Special designs, such as anti-corrosion, anti-explosion, and antiseismic designs
  Suitable for the design and planning of projects with innovative requirements
  Suitable for projects using government or international organization funds and with special demands on PUE
Global average wet-bulb temperature distribution
Chilled water +
plate heat exchanger
Direct
ventilation cooling
Indirect
evaporative cooling

## Slide 33: Indirect Evaporative Cooling System Configuration Process
Requirement specifications input
Air inlet and outlet specifications design
Cooling load calculation
Control logic determination
Main device selection
Device selection and calculation
Device configuration list output
Design Point |  | 
Redundancy mode |  | N, (N+1), (N+X)
Main device type | Cooling source and refrigerant | Indirect evaporative cooling system + DX stepless load adjustment (R407C/R410A)
 | Fan | Variable-frequency or constant-frequency fans on the primary and secondary sides
 | Air-to-air heat exchanger | Metal plate or non-metal tube type
 | Evaporative cooling | Water sprinkling/spraying
Control logic | Dry working condition | Outdoor air dry-bulb temperature ≤ Critical dry-bulb temperature under dry working conditions
 | Wet working condition | Critical dry-bulb temperature under dry working conditions < Temperature after adiabatic evaporation of the outdoor air ≤ Critical wet-bulb temperature under wet working conditions
 | Wet working condition + compressor hybrid working condition | Temperature after adiabatic evaporation of the outdoor air > Critical wet-bulb temperature under wet working conditions
Notes: The yellow parts indicate the key points described in this slide for indirect evaporative cooling system configuration and selection.
Requirement specifications input: cabinet power density, cabinet quantity, data center area, and data center environment specifications (dry-bulb temperature, relative humidity, particle concentration, and harmful gas concentration)
Air inlet and outlet specifications design: After the air inlet and outlet specifications are determined, the air volume can be calculated to determine the supply air volume and exhaust air volume. Device selection information can be provided to the device vendor to configure the rotary wheel.
Control logic determination: Determine the control logic of the full rotary wheel, hybrid, and full compressor working conditions.
Main device selection: The integrated solution of the rotary wheel free cooling consists of many functional sections. Identify mandatory and optional sections, and determine the selection basis.
Device selection and calculation: The selection specifications of the rotary wheel free cooling air conditioner include the air volume, air pressure, environment specifications, air inlet and outlet specifications, cooling capacity, humidification capacity, cleanliness, and noise requirements.
Device configuration list output: Output the list based on the preceding selection solution.

## Slide 34: Key points for Indirect Evaporative Cooling System Configuration (1)
Specifications input
Air inlet and outlet specifications design
  Supply and return air specifications for indirect evaporative cooling
Specifications Input
Tier requirements
Total power consumption of computers (kW)
Common number of personnel in the data center
Cabinet power density (kW/rack)
Climate level and type
Area of each room in the data center (computer room, power room, and auxiliary area)
Outdoor temperature and humidity
Control logic determination (The following is an example. The temperature for mode switching can be adjusted based on the actual situation.)
  Outdoor air dry-bulb temperature ≤ 20°C
  The fan on the primary side runs at full speed, the compressor stops, and the evaporative cooling system does not run. The drive motor frequency of the fan on the secondary side is adjusted steplessly within the range of 5 Hz to 50 Hz based on the outlet air temperature of the fan on the primary side.
  20°C < Outdoor air wet-bulb temperature ≤ 22°C
  The fan on the primary side runs at full speed, the compressor stops, and the evaporative cooling system starts. The drive motor frequency of the fan on the secondary side is adjusted steplessly within the range of 5 Hz to 50 Hz based on the outlet air temperature of the fan on the primary side.
  Outdoor air wet-bulb temperature > 22°C
  The fans on the primary and secondary sides run at full speed. The evaporative cooling system starts. The compressor starts and performs stepless load adjustment based on the outlet air temperature of the fan on the primary side.

## Slide 35: Key points for Indirect Evaporative Cooling System Configuration (2)
Main device selection
No. | Functional Section | Technical Description
1 | Air filter | Filters and purifies the primary side return air and secondary side fresh air. The primary filter is of class G4.
2 | Air-to-air heat exchanger | Performs indirect heat exchange between the primary air side and the secondary air side.
3 | Evaporative cooling device | Performs evaporative cooling on the outdoor air on the secondary side.
4 | Fan | Supplies circulating power to the circulating air on the primary side and the outdoor fresh air on the secondary side. DC inverter EC fans are adopted to minimize energy consumption and noise.
5 | Backup mechanical cooling cycle | Includes DX and chilled water types; supplements the cooling capacity when indirect evaporative cooling provides insufficient cooling capacity in extreme outdoor temperatures.
6 | Air conditioner shell | High-quality flame-retardant polyurethane thermal insulation materials are used in the middle of the double-layer panel, and cold bridges and condensation are prevented.
7 | Control system | Controls the operation of the air conditioner and reserves ports for connecting to the teamwork control system.
Notes: Air filter: Because of indirect heat exchange, the indoor air and outdoor air are completely isolated, and no cross pollution occurs. Generally, air filters of only one class need to be configured on both sides. The filtering level is usually G4.
Air-to-air heat exchanger: Generally, metal plate heat exchangers and non-metal tube heat exchangers are used. Heat pipe heat exchangers are seldom used due to their high costs. During the selection of heat exchangers, the heat exchange efficiency requirements under dry and wet working conditions are mainly considered to select proper air-to-air heat exchangers.

## Slide 36: Key points for Indirect Evaporative Cooling System Configuration (2)
Main device selection
No. | Functional Section | Technical Description
1 | Air filter | Filters and purifies the primary side return air and secondary side fresh air. The primary filter is of class G4.
2 | Air-to-air heat exchanger | Performs indirect heat exchange between the primary air side and the secondary air side.
3 | Evaporative cooling device | Performs evaporative cooling on the outdoor air on the secondary side.
4 | Fan | Supplies circulating power to the circulating air on the primary side and the outdoor fresh air on the secondary side. DC inverter EC fans are adopted to minimize energy consumption and noise.
5 | Backup mechanical cooling cycle | Includes DX and chilled water types; supplements the cooling capacity when indirect evaporative cooling provides insufficient cooling capacity in extreme outdoor temperatures.
6 | Air conditioner shell | High-quality flame-retardant polyurethane thermal insulation materials are used in the middle of the double-layer panel, and cold bridges and condensation are prevented.
7 | Control system | Controls the operation of the air conditioner and reserves ports for connecting to the teamwork control system.
Notes: Evaporative cooling device: There are two types of evaporative cooling methods. One is similar to the principle of a cooling tower. Water is directly sprayed on an air-to-air heat exchanger and contacts with the outdoor air on the secondary side to absorb heat and lower the temperature. The other is adiabatic spray, in which water does not directly contact with the air-to-air heat exchanger. Water is sprayed on the outdoor air on the secondary side for adiabatic humidification and cooling, and then the heat of the cooled air is exchanged with that of the indoor air on the primary side through an air-air heat exchanger.
Fan: includes fans on the primary and secondary sides. Motors are configured for the fans.
Backup mechanical cooling cycle: includes DX evaporator and chilled water coil types.
Air conditioner shell: The panel material, thickness, thermal insulation material, structure strength, anti-air leakage, anti-cold bridge, and anti-condensing function are mainly considered for the shell. The maximum air leakage rate of the air conditioner should not be greater than 1%. The cold bridge factor should reach TB2 or higher of the EN 1886 standard. There should be no cold bridge.
Control system: usually delivered with the air conditioner. The PLC controller can be integrated with the air conditioner or remotely installed indoors. The control system has a color touchscreen whose size is not less than 7 inches, provides anti-freezing and anti-condensing control functions, and provides RS232 and RS485 ports (Modbus protocol) that support remote control and centralized management.

## Slide 37: Key points for Indirect Evaporative Cooling System Configuration (3)
Main device selection: The main design specifications of the indirect evaporative cooling air conditioner include air volume, air pressure, environment specifications, air inlet and outlet specifications, cooling capacity, adiabatic humidification capacity, cleanliness, and noise requirements, as shown in the following tables.
Type | Item | Design Specifications
Ventilation system | Air volume on the primary side | Calculated based on the cooling load and supply and return air specifications
 | External static pressure of the fan on the primary side | Calculated based on the resistance of the air duct system
 | Motor power consumption | Determined based on the air volume, total fan pressure, and efficiency
 | Air volume on the secondary side | Generally, the maximum air volume is the same as that on the primary side.
 | External static pressure of the fan on the secondary side | It is used to overcome the resistance of the components in the system.
 | Motor power consumption | Determined based on the air volume, total fan pressure, and efficiency
Indirect evaporative cooling system | Cooling capacity supply | Determined based on load calculation
Compressor cooling system | Cooling capacity | If 100% backup is required, the cooling capacity is the indirect heat exchange cooling capacity. If only partial load backup is required, the cooling capacity is determined based on the actual proportion.
 | Compressor power consumption | Configured based on the system

## Slide 38: Key points for Indirect Evaporative Cooling System Configuration (3)
Main device selection: The main design specifications of the indirect evaporative cooling air conditioner include air volume, air pressure, environment specifications, air inlet and outlet specifications, cooling capacity, adiabatic humidification capacity, cleanliness, and noise requirements, as shown in the following tables.
Evaporative cooling and humidification system | Humidification capacity | Calculated based on the maximum air volume and maximum humidity difference on the secondary side
 | Water consumption | Determined based on the humidification capacity, humidification efficiency, and water circulation logic
Provided Specifications | Customization | Key Device
Air volume | Fan | Fan on the primary side
Air pressure |  | Fan on the secondary side
Noise |  | Muffler (optional)
Environmental specifications | Air-to-air heat exchanger | Air-to-air heat exchanger
Air intake and exhaust specifications |  | 
Cooling capacity | Cooling system | Compressor
 |  | Evaporator
 |  | Condenser
Humidification capacity | Adiabatic evaporative humidifier | Adiabatic evaporative humidifier
Cleanliness | Filtering section | G4 bag filter

## Slide 39
Free Cooling Solution Configuration for Data Center Air Conditioners
Continuous Cooling Solution Configuration for Data Center Air Conditioners
Configuration Cases for Data Center Air Conditioning Systems

## Slide 40: Continuous Cooling Concept
A data center that requires high reliability or high density must have the continuous cooling function.
  Short-time cooling interruption may be tolerated in low-density data centers, but may cause faults or even service interruption in medium- and high-density data centers.
A diesel generator (DG) alone cannot guarantee continuous cooling.
  When the mains supply is cut off, cooling is also interrupted. It takes 5 to 15 minutes for the DG to start, the compressor to restart, and the cooling to recover.
Cooling duration without air conditioners
Once the air conditioning system in a data center is interrupted, the temperature of the data center rises rapidly, which may cause server faults or even breakdown.
Average intake air temperature
of the cabinet
Time required for the 500 TR unit to return to the preset chilled water temperature
High load
Standard unit
-Low load
UPS quick startup
-High load
UPS quick startup
-Low load
Low load: 3 minutes and 2 seconds
High load: 5 minutes and 30 seconds
Notes: When the air conditioner stops running, the time for server breakdown is calculated as follows:
  < 2 kW/cabinet (< 500 W/m2): The server breaks down 12 minutes after the air conditioner stops running.
  3 kW/cabinet: The server breaks down 8 minutes after the air conditioner stops running.
  6 kW/cabinet: The server breaks down 3 minutes after the air conditioner stops running.
  9 kW/cabinet: The server breaks down 2 minutes after the air conditioner stops running.
  15 kW/cabinet: The server breaks down 1 minute after the air conditioner stops running.
It takes at least 2 minutes for the chiller to resume cooling after shutdown.

## Slide 41: Uptime White Paper – Continuous Cooling (1)
The main function of continuous cooling is to eliminate the short-time cooling capability loss during the transfer between the mains and the DG.
Basic requirement | Only Tier IV data centers require continuous cooling. It is recommended that continuous cooling be configured if the rated power density exceeds 4 kW/rack regardless of the data center tier.
Continuous cooling time | Regardless of technical factors, continuous cooling is defined as the capability of providing stable and uninterrupted cooling for IT devices and UPSs. During the UPS backup time, the continuous cooling system provides stable cooling capability. For example, the static UPS system provides 15-minute backup power. The continuous cooling system should provide stable cooling during the 15 minutes. If there are redundant modules and batteries, the backup time of 15 minutes may be extended to 30 minutes or longer. Customers must exercise caution when determining whether to configure continuous cooling based on the specified backup time or available backup time. The cooling system recovery time must be set no matter what types of cooling and UPS technologies are used. For example, in a chilled water system, although the power supply of the DG can be recovered within several seconds, it takes 15 minutes or even longer for the chiller to recover after a power failure. Therefore, the cooling storage time must be considered based on the backup time and the time required for the cooling system to restore stable cooling.
Notes: According to the white paper on the continuous cooling system for high-density data centers discussed by the Uptime Institute, cooling systems are classified into classes A, B, and C. Class A is the uninterruptible cooling system, which requires UPSs to be configured for fans and secondary pumps of precision air conditioners, and also requires a thermal storage tank. Class B is the continuous cooling system, which requires UPSs to be configured for fans and secondary pumps of precision air conditioners, but does not require a thermal storage tank. Class C is the interruptible cooling system, which requires no UPS and is stopped when the power supply is faulty.
Suggestions of Uptime:
  When the power consumption exceeds 4 kW/cabinet, continuous cooling (cooling storage) can be considered.
  When the power consumption exceeds 6 kW/cabinet, continuous cooling is recommended.

## Slide 42: Uptime White Paper – Continuous Cooling (2)
The main function of continuous cooling is to eliminate the short-time cooling capability loss during the transfer between the mains and the DG.
Chilled water system | It has the cooling storage capability. The secondary pump and indoor unit are powered by the UPS. It uses the same UPS with the IT device or a separate UPS that supports online maintenance and fault tolerance. If a primary pump is used, it must be powered by the UPS.
DX system | Both indoor and outdoor units are powered by the UPS that is maintained online and is fault-tolerant. The same requirement applies to split-type air conditioning systems.
100% free cooling system | Fans or other systems that transfer outdoor cold air indoors must be powered by the UPS.
Notes: According to the white paper on the continuous cooling system for high-density data centers discussed by the Uptime Institute, cooling systems are classified into classes A, B, and C. Class A is the uninterruptible cooling system, which requires UPSs to be configured for fans and secondary pumps of precision air conditioners, and also requires a thermal storage tank. Class B is the continuous cooling system, which requires UPSs to be configured for fans and secondary pumps of precision air conditioners, but does not require a thermal storage tank. Class C is the interruptible cooling system, which requires no UPS and is stopped when the power supply is faulty.
Suggestions of Uptime:
  When the power consumption exceeds 4 kW/cabinet, continuous cooling (cooling storage) can be considered.
  When the power consumption exceeds 6 kW/cabinet, continuous cooling is recommended.

## Slide 43: Solutions for Continuous Cooling in High-Density Data Centers
For a data center that uses the chilled water system, the continuous cooling measures are as follows: Install a thermal storage device for the cooling source system (the cooling storage time should be at least 15 minutes). Use UPSs to supply power to the control system, indoor unit chilled water circulating pump, and air conditioner fan.
For a data center that uses the air-cooled DX air conditioning system, the continuous cooling measure is as follows: Use UPSs to supply power to the indoor and outdoor units.
For a data center that uses a direct or indirect evaporative cooling system, the continuous cooling measure is as follows: Use UPSs to supply power to the indoor unit cooling water pump and distributed fan.
For a data center that uses the direct fresh air cooling system, the continuous cooling measure is as follows: Use UPSs to supply power to the inlet and outlet fans that support cooling.

## Slide 44: Continuous Cooling Configuration for the Chilled Water Air Conditioning System (1)
Parallel running:
In cooling storage mode, chilled water flows in from the bottom and out from the top.
In cooling release mode, chilled water is supplied from the bottom and returned from the top.
Set the temperature sensor along the vertical direction of the thermal storage tank.
In the Tier 3 architecture, the thermal storage tank does not require redundancy. You can perform online maintenance as planned by disconnecting the motorized valve.
In the Tier 4 architecture, the thermal storage tank does not require redundancy and meets the 2N architecture requirements.
Automatic cut-off valves are configured for the water inlet and outlet pipes of the thermal storage tank.
A thermal storage tank is a chilled water storage device. It uses the water distribution system to layer water of different temperatures based on the different densities of water at different temperatures. This prevents cooling loss caused by mixing of cold water and warm water. Generally, the thermal storage tank includes the water tank body, water distributor, liquid level meter, temperature measuring components, thermal insulation layer, ladder, railings, and surge protection devices.
Cooling architecture of a Tier 3 data center with a thermal storage tank

## Slide 45: Continuous Cooling Configuration for the Chilled Water Air Conditioning System (2)
Calculation of the volume of the water storage tank
  The volume of the water storage tank can be calculated as follows:
  L: designed volume (m3) of the water storage tank
  Q: designed cooling storage capacity (kWh) of the water storage tank
  K: performance index of the water storage tank. It refers to the ratio of the output energy to the input energy of the water storage tank in a cooling storage and release period. The value ranges from 0.85 to 0.9.
  ρ: water density (kg/m3)
  c: specific heat capacity of water [kJ/(kg·K)]
  Δt: temperature difference (K) between the supply and return water of the water storage tank

## Slide 46
Free Cooling Solution Configuration for Data Center Air Conditioners
Continuous Cooling Solution Configuration for Data Center Air Conditioners
Configuration Cases for Data Center Air Conditioning Systems

## Slide 47: Overview of the Air Conditioning System in a Data Center - Outdoor Environment
Outdoor air calculation specifications
Construction Site | Calculated Dry-Bulb Temperature of the Air Conditioner |  | Calculated Dry-Bulb Temperature for Ventilation |  | Calculated Outdoor Wet-Bulb Temperature of the Air Conditioner in Summer | Calculated Relative Humidity of the Air Conditioner in Winter | Calculated Outdoor Relative Humidity for Ventilation in Summer | Calculated Average Daily Temperature of the Air Conditioner in Summer | Outdoor Average Wind Speed in Winter
Guiyang | Winter: –2.5°C | Summer: +27.1°C | Winter: –2.5°C | Summer: +27.1°C | +23°C | 80% | 64% | +26.5°C | 2.1 m/s
The annual outdoor wet-bulb temperature in Guiyang is less than or equal to 7°C for about 2251 hours, accounting for 25.7% of the year. The free cooling source can be fully used for about 93 days.

## Slide 48: Overview of the Air Conditioning System in a Data Center - Data Center Overview
Indoor calculation specifications
Data center scale
  The data center is planned to house 2202 IDC cabinets. If the power of each cabinet is 7 kW, the total IT power consumption is 12,331 kW, and the total cooling load of air conditioners in summer is about 15,400 kW.
Air conditioning system planning analysis
  A cooling source system with large- and small-capacity air conditioner chillers is adopted. In the early stage of the building, the small-capacity chiller is used when the installed capacity is small. This prevents the large-capacity chiller from running at low load, which improves the cooling efficiency of the air conditioner, reduces energy consumption of the air conditioner, and lowers the PUE value at the initial phase of data center construction. When the installed capacity reaches a certain value, the large-capacity chiller is used to ensure that the air conditioner works in a high-efficiency range. This prevents the centrifuge chiller from generating surges when the load is low. The chillers are started based on the load. The large-capacity chiller runs at full load.
Item | Description | Remarks
Temperature in the cold aisle or the air intake area of the cabinet | 18–27°C | Dew formation is not allowed.
Relative humidity and dew point temperature in the cold aisle or the air intake area of the cabinet | The dew point temperature ranges from 5.5°C to 15°C, and the relative humidity is less than or equal to 60%. | 
Temperature and relative humidity of the auxiliary area (when equipment is powered on) | Temperature: 18–28°C; relative humidity: 35%–75% | 
Temperature of the UPS and battery room | 20°C–30°C | 
Notes: The centrifugal chiller generates surge at a load rate below 30%.

## Slide 49: Overview of the Air Conditioning System in a Data Center - Solution Configuration (1)
The figure on the left shows the flowchart of the chilled water air conditioning system in a data center of a project in Guiyang.
1. Centrifugal chiller: 700 USRT
2. Centrifugal chiller: 1400 USRT
3. Plate heat exchanger: 2800 kW
4. Plate heat exchanger: 5600 kW
5. Primary chilled water pump: 390 m3/h
6. Primary chilled water pump: 780 m3/h
7. Secondary chilled water pump: 390 m3/h
8. Secondary chilled water pump: 780 m3/h
9. Cooling water pump: 540 m3/h
10. Cooling water pump: 1080 m3/h
11. Cooling tower: 2500 kW in summer
12. Cooling tower: 5900 kW in summer

## Slide 50: Overview of the Air Conditioning System in a Data Center - Solution Configuration (2)
In this project, a single data center is planned to house three high-voltage variable-frequency 1400 RT chillers, one low-voltage variable-frequency 700 RT chiller, and related auxiliary devices. Air conditioner devices, such as chillers, are placed in the bottom-layer chiller plant, and the open crossflow cooling tower is placed on the roof. The supply and return chilled water temperatures are 10°C and 16°C, respectively. The supply and return cooling water temperatures are 30°C and 35°C, respectively. When the data center is running with full load, start the 4200 RT chillers. The following table lists the solution configuration.
No. | Device Name | Device Model | Device Quantity | Rated Capacity of a Single Device
 |  |  | (PCS) | (kW)
1 | Centrifugal chiller (10 kV) | Rated cooling capacity: 1400 USRT 10°C/16°C | 3 | 815
 | Centrifugal chiller (380 V) | Rated cooling capacity: 700 USRT 10°C/16°C | 1 | 381
2 | Plate heat exchanger | Heat exchange capacity: 5600 kW 10°C/16°C and 8.5°C/13.5°C | 3 | N/A
 |  | Heat exchange capacity: 2800 kW 10°C/16°C and 8.5°C/13.5°C | 1 | N/A
3 | Primary chilled water circulating pump | Flow rate: 780 m3/h Lift: 18 m | 3 | 55
 |  | Flow rate: 390 m3/h Lift: 18 m | 1 | 37
Chiller configuration
  The total cooling load is 15,400 kW. Generally, two to four chillers are recommended. For a small-or medium-sized data center, two chillers are recommended. For a large-sized data center, three chillers are recommended. For a hyperscale data center, four chillers are recommended. In this example, three 1400 RT (4923 kW) chillers are selected. Besides, one 700 RT unit (2461 kW) is configured to meet the cooling requirements for low-load operation in the early stage.
Plate heat exchanger configuration
  Determine the heat exchange capacity: Q1 = 4923 x 1.1 ≈ 5600 kW; Q2 = 2461 x 1.1 ≈ 2800 kW.
  Determine the supply and return water temperatures on the primary side: 10°C/16°C.
  Determine the supply and return water temperatures on the secondary side: 8.5°C/13.5°C.
Primary chilled water circulating pump
  Determine the flow rate: 0.86 x 4923 x 1.1/6 = 776 m³/h; 0.86 x 2461 x 1.1/6 = 388 m³/h.
  Determine the lift: 18 m (estimated).

## Slide 51: Overview of the Air Conditioning System in a Data Center - Solution Configuration (3)
In this project, a single data center is planned to house three high-voltage variable-frequency 1400 RT chillers, one low-voltage variable-frequency 700 RT chiller, and related auxiliary devices. Air conditioner devices, such as chillers, are placed in the bottom-layer chiller plant, and the open crossflow cooling tower is placed on the roof. The supply and return chilled water temperatures are 10°C and 16°C, respectively. The supply and return cooling water temperatures are 30°C and 35°C, respectively. When the data center is running with full load, start the 4200 RT chillers. The following table lists the solution configuration.
No. | Device Name | Device Model | Device Quantity | Rated Capacity of a Single Device
 |  |  | (PCS) | (kW)
4 | Secondary chilled water circulating pump | Flow rate: 780 m3/h Lift: 25 m | 3 | 75
 |  | Flow rate: 390 m3/h Lift: 26 m | 1 | 55
5 | Cooling water pump | Flow rate: 1080 m3/h; lift: 30 m | 3 | 110
 |  | Flow rate: 540 m3/h Lift: 30 m | 1 | 75
6 | Cooling tower | Heat dissipation capacity: 5900 kW in summer (30°C/35°C; Ts = 25); 5100 kW in winter (8.5°C/13.5°C; Ts = 4) | 3 | 74
 |  | Heat dissipation capacity: 2500 kW in summer (30°C/35°C; Ts = 25); 2600 kW in winter (8.5°C/13.5°C; Ts = 4) | 1 | 37
Secondary chilled water circulating pump
  Determine the flow rate: The calculation method is the same as that of the primary pump. (You can also calculate the flow rate based on the heat exchange capacity of the plate heat exchanger and the temperature difference between the supply and return water on the secondary side.)
  Determine the lift: 25 m and 26 m (estimated).
Cooling water pump
  Determine the flow rate: 0.86 x (4923 + 815) x 1.1/5 ≈ 1080 m³/h.
  0.86 x (2461 + 381) x 1.1/5 = 540 m3/h
  Determine the lift: 25 m and 26 m (estimated).
Cooling tower
  Heat dissipation capacity: 5900 kW in summer; 5100 kW in winter
  Heat dissipation capacity: 2500 kW in summer; 2600 kW in winter

## Slide 52
Data Center Air Conditioning System Performance Optimization Method
Free Cooling Solution Configuration for Data Center Air Conditioners
Continuous Cooling Solution Configuration for Data Center Air Conditioners
Configuration Cases for Data Center Air Conditioning Systems

## Slide 53
(Single) In the water-cooled chilled water + indirect free cooling solution, which equipment can implement heat exchange between cooling water and chilled water without consuming power?
  Cooling tower
  Chiller
  Chilled water tank
  Plate heat exchanger
Notes: Answer: D

## Slide 55
Shenjutao/WX352174
2020.10.01
Lishaofeng/00486775