## Slide 1: DCIM System Architecture and Functions

## Slide 2
This chapter introduces the physical architecture, logical architecture, and system functions of DCIM.

## Slide 3
On completion of this course, you will be able to:
  Describe DCIM physical architecture.
  Describe DCIM physical deployment layers.
  Describe DCIM logical architecture.
  Describe DCIM system functions.

## Slide 4
DCIM Hardware Physical Architecture
DCIM Logical Architecture and System Functions
DCIM System Performance and Integration

## Slide 5: DCIM Hardware Physical Architecture (1)
The physical architecture reflects DCIM physical components and relationships between these components. In the DCIM system, components are deployed at physical layers to support system running.
Generally, a complete DCIM system consists of intelligent interfaces and sensors, collection devices, processing and storage devices, display devices, and network transmission devices.
Intelligent interfaces and sensors
Collection devices
Processing and storage devices
Display devices
Network transmission devices
Notes: Sensors: include temperature and humidity sensors, smoke sensors, infrared sensors, and water (leakage) sensors.
Collection devices: Currently, intelligent collection units are most widely used. The collectors not only transparently transmit signals, but also adapt to devices of different protocol types and provide standard access protocols. Collectors also include power and environment monitoring instruments and serial port servers. These collectors only provide transparent transmission of signals.
Processing and storage devices: Processing and storage devices are the physical core of the DCIM system. They process, compute, and store system data, and provide the system software running environment and operating system.
Display devices: They are the man-machine interaction interface of the DCIM system and are used to input and output system information. Common display devices include large screens, email, SMS, and audible and visual devices.
Network transmission devices: include network transmission media and corresponding connection devices. Common transmission media involve twisted pairs, coaxial cables, optical fibers, and wireless transmission media. Common connection devices include hubs, switches, and routers. In some special scenarios, firewalls for network filtering and load balancers for load balancing in cluster systems are required.

## Slide 6: DCIM Hardware Physical Architecture (2)
Sensors
A sensor is a device that senses a measured object and produces an available signal for output according to certain rules. Generally, a sensor consists of a sensitive element that directly senses a measured object, a transfer element that produces an available signal, and an auxiliary electronic circuit. Common sensors include temperature and humidity sensors, smoke detectors, infrared sensors, and water (leakage) sensors.
Collection devices
In the DCIM system, a collection unit is also referred to as a collector, and is used to collect running data of a device or a sensor in a polling manner. Currently, intelligent collection units, such as Huawei ECC800 and Vertiv (Emerson) FSU, are widely used. These collectors not only transparently transmit signals, but also adapt to devices of different protocol types and provide standard access protocols. Collectors also include power and environment monitoring instruments and serial port servers. These collectors only provide transparent transmission of signals.
Processing and storage devices are the physical core of the DCIM system. They process, calculate, and store system data, and provide the system software running environment and operating system. For example, Huawei TaiShan server.
Notes: Transparent signal transmission: In this mode, content is transmitted from the source address to the destination address without any change to its data.

## Slide 7: DCIM Hardware Physical Architecture (3)
Processing and
storage devices
Processing and storage devices are the physical core of the DCIM system. They process, calculate, and store system data, and provide the system software running environment and operating system. For example, Huawei TaiShan server.
Display devices
A display device is a man-machine interaction interface of the DCIM system and is used to input and output system information. Common display devices involve large screens, mobile terminals, email, SMS, and audible and visual alarm devices.
Network
transmission devices
Network transmission devices include network transmission media and corresponding connection devices. Common transmission media involve twisted pairs, coaxial cables, optical fibers, and wireless transmission media. Common connection devices include hubs, switches, and routers. In some special scenarios, firewalls for network filtering and load balancers for load balancing in cluster systems are required.
Notes: Hub: A hub is a basic communication device that physically connects nodes on a multi-point bus or loop. It is generally used in Ethernet and a Fibre Channel network to improve the manageability of physical cables. While forming a new hub-and-spoke star physical structure, the hub also maintains the logical loop structure of the network to which the hub belongs. Unlike switches, hubs do not aggregate network bandwidth. A hub generally supports the addition and removal of nodes on the bus.
Switch: A switch is a basic network component that can connect multiple network nodes. Different from a hub, a switch generally has internal bandwidth, which is an integer multiple of the link bandwidth, and can quickly switch node connections. A typical switch can process full-link bandwidth transmission that occurs simultaneously between multiple pairs of nodes.

## Slide 8
Notes: Router: A device at the network layer. Routers can be used to select routes on the Internet. A router selects a proper route (through a network) based on the destination address of a received packet and sends the packet to the next router. The last router in the route sends the packet to the destination host. It can be used to connect a local network to another local network, a wide area network to another wide area network, or a local network to the Internet.
Firewall: A collection of components configured between different networks or network security domains. A firewall monitors, restricts, and changes data flows across the firewall to shield the internal information, structure, and running status of the network. In this way, the network security is protected.
Load balancer: A load balancer is a hardware device that distributes network requests to available servers in a server cluster, manages incoming web data traffic, and increases effective network bandwidth.

## Slide 9: DCIM Physical Deployment Layers
Power distribution infrastructure
UPS
PDF
BAT
DG
Environment infrastructure
A/C
T/H sensor
Water sensor
Fire extinguishing system
Controller
Smoke sensor
Security protection system
Video surveillance
Access control
Device layer
Collection layer
Intelligent collection unit
Switch
or
Management layer
Active server
Standby server
and
Display layer
Web client (B/S)
Mobile client
Local client (C/S)
or
Large-screen display
Access mode
Display mode
Email
SMS
Notes: This slide shows common DCIM physical deployment layers.

## Slide 10
DCIM Physical Hardware Architecture
DCIM Logical Architecture and System Functions
  DCIM Logical Architecture
  DCIM System Functions
DCIM System Performance and Integration

## Slide 11: DCIM Software Logical Architecture
The logical architecture covers logical components of monitoring management system software and relationships between these logical components. Generally, the system consists of the following four basic components: monitoring system, operation management system, general control system, and basic service system.
General control system
Monitoring system
Operation management system
Basic service system
O&M management
Asset
management
Capacity
management
…
System
management
Rights
management
Service
management
…
Signal
management
Mobile access
View
management
…
Information
collection
Information
processing
…
Notes: Monitoring system:
  Information collection system: To implement modular design, the information collection system is usually deployed in distributed mode to improve the stability of the monitoring and management system. The information collection system is basically hardware-based.
  Information processing system: The information processing system is the core equipment or module that implements monitoring in the monitoring and management system. Instead of the traditional software-based information collection subsystem, the information processing system processes, calculates, and stores a large amount of data in real time, flexibly, and accurately.
Operation management system:
  Asset management: includes assets warehousing, allocating, unallocating, and scrapping.
  Capacity management: refers to the capacity management of (U) space, power, cooling, network (SPCN), that is, the capability of supporting infrastructure such as power, cooling, space, and network of a data center.
  O&M management: ensures the stable running of a data center and is also the main task of routine management of the data center. It supports activities such as troubleshooting, routine maintenance, periodic inspection, and personnel duty management of the data center.

## Slide 12
Notes: General control system:
  Signal management: The system displays key device information in real time and allows users to filter, search for, and mask data.
  View management: The system provides multiple methods to intuitively display data center device information, alarm information, O&M bulletins, and to-do tasks.
  Mobile access: In addition to local access and interaction, the system also supports mobile terminal access to implement mobile information viewing and mobile O&M.
Basic service system:
  System management: The system provides user management, login management, security policy management, and software upgrade.
  Service management: manages service licenses and network element (NE) mediations of the DCIM system.
  Rights management: performs DCIM system user management and login control.

## Slide 13: Monitoring System
The DCIM monitoring system consists of the information collection system and information processing system.
Information processing system:
  The system collects, stores, and processes system information.
  The system receives data from the information collection system and processes the data.
Information collection system:
  The system collects information such as the status, parameters, running data, device attributes, and configurations of critical infrastructures, and transmits the collected information to the information processing system based on preset standards and requirements.
Key Facilities
Power supply and distribution devices
Cooling devices
Environment devices
Security protection devices
…
Monitoring system
Information collection system
Information processing system
O&M transactions
Alarm generation
Real-time display
O&M support
…
Notes: The monitoring system can display the alarm information of the current data center in real time. In addition, it can perform alarm notification and convergence management based on the preset mode, such as SMS notification, email notification, and work order dispatch.
The prerequisite for the DCIM system to complete data processing, analysis, and optimization is that the system has a complete information collection function.
Information processing system:
  Generates new alarm information based on alarm rules, and associates, compresses, and filters massive alarm information to locate faults.
  Sends important monitoring information to the general control system for real-time display.
  Manages related information to implement the corresponding management process.
  Stores and manages other important data, generates historical data for the operation management system to invoke, and produces statistical analysis reports as required.

## Slide 14: Operation Management System
The DCIM system implements functions such as O&M management, energy efficiency management, asset management, and capacity management based on the routine operation of data center infrastructure to improve the data center availability, optimize management, and reduce operating expenses (OPEXs).
Operation management system
Capacity management
The DCIM system provides functions such as capacity analysis, configuration, design, and report based on the SPCN consumption of a data center.
O&M management
It refers to a series of routine, regular, or temporary maintenance and repair work and personnel management for critical infrastructure. Generally, O&M management provides following functions: (electronic) inspection, routine drill, maintenance, repair management, risk management, personnel scheduling, shift handover record, and supplier management.
Asset management
The DCIM system provides functions such as asset analysis, asset records, warehouse management, asset stocktaking, asset configuration, and asset report based on monitoring information.
Energy efficiency management
Based on collected energy consumption data, the DCIM system implements operations such as energy consumption measurement, statistics collection, analysis, display, report generation, and proactive optimization.
Notes: SPCN: (U) space, power, cooling, network.

## Slide 15: General Control System
The general control system provides a user interface for O&M personnel to monitor the running status of a data center and interact with the data center. The user interface provides common routine O&M functions, such as view management, signal management, and service desk.
General control system
View management
Signal management
Service desk
After the DCIM system is configured, the general control system can display the physical topology, micro-module view, and cabinet view of a data center in multiple modes, such as 2D, 2.5D, 3D, and large screen.
Key indicators such as the running and alarm information of key devices in a data center can be displayed on the signal management page. A user can filter, search for, and mask the indicators based on actual O&M requirements.
O&M personnel can use the service desk to complete various O&M tasks, such as dispatching O&M tasks, tracking task progress, processing to-do tasks, and releasing project bulletins.

## Slide 16: Basic Service System
The basic service system provides some common basic services for the preceding logical components, such as unified permission management, service management, and system management.
Basic service system
Rights management is critical to the secure running of data centers， including user management, role management, right delivery, and region management.
Includes the license validity period and mediation management of DCIM functions.
Includes log management, security management, and software management.
Provides other basic services that support system running, such as system time, protocol switch, and network address translation (NAT).
Rights management
Service management
System management
Other basic services

## Slide 17
DCIM Physical Architecture
DCIM Logical Architecture and System Functions
  DCIM Logical Architecture
  DCIM System Functions
DCIM System Performance and Integration

## Slide 18: DCIM System Functions
To achieve management objectives, the DCIM system must provide various management functions. According to the logical architecture, the DCIM system functions can be divided into four parts: monitoring, operation management, general control, and basic services.
Monitoring
Operation management
General control
Basic services
Notes: DCIM management objective: To achieve maximal possible availability of a data center with minimal operating costs.
Monitoring: The DCIM system collects, analyzes, stores, and displays data, enabling O&M personnel to understand the running status of data center infrastructure in real time.
Operation management: O&M personnel use the DCIM unified management platform to implement data center operation management and improve data center availability.
General control: It is the entrance to DCIM O&M management and provides an interaction portal for O&M personnel. Generally, it includes routine management functions such as service desk, view management, and signal display.
Basic services: They refer to system functions provided by the DCIM system to implement management functions, including user and rights management, system management, and system service management.

## Slide 19: Monitoring
The DCIM system collects, analyzes, processes, and stores data, and generates alarms, enabling O&M personnel to understand the running status of data center infrastructure in real time.
Collection
Transmission
Storage
Regulation and control
Collects data by monitoring objects in real time.
Processing
Alarm
Monitoring
The collected data can be transferred between nodes based on transmission policies.
The collected data can be computed, analyzed, and processed based on service requirements.
The collected data needs to be stored for system computing and historical data query.
The system remotely controls the working mode and status of the infrastructure.
The system compares the collected information with the preset or user-defined alarm rules. If the collected information meets the rules, a warning or alarm is generated.
Notes: Collection: The monitoring system monitors various objects in real time, collects data, and uploads the collected data in a unified format to the data processing layer for unified processing. The monitoring system also performs basic filtering on the collected data to avoid false alarms.
Transmission: The collected data can be transferred between nodes in the system based on transmission policies. Multiple transmission policies and data processing modes are supported. Monitoring data streams can be transferred through conventional polling-based centralized transmission or more efficient proactive reporting transmission. To ensure the security of the information system, the system can encrypt monitoring data streams, especially sensitive data.
Processing: The collected data can be computed, analyzed, and processed based on service requirements. The system can preset or customize data computing rules and complex event processing rules to meet various processing requirements.

## Slide 20
Notes: Storage: The collected data needs to be stored for system computing and historical data query. Generally, a data processing system needs to perform real-time computing, which requires a high real-time performance of a storage system. The real-time database stores the real-time data in the memory to ensure the real-time performance. In addition, the system needs to perform statistical analysis on historical data collected to generate data center-related reports, providing a basis for data center operation. In the system, a history database stores the collected data to the disk medium according to the time sequence for the system to invoke.
Adjustment and control: The system can remotely control the working mode and status of infrastructure devices. The control mode can be manual or automatic.
Alarm: The system can compare the collected information with the preset or user-defined alarm rules. When the conditions are met, a warning or alarm is generated. In addition, the system can send feedback notifications based on preset interaction modes, such as SMS, emails, and audible and visual alarms.

## Slide 21: Operation Management
Operation management enables O&M personnel to use the DCIM unified management platform to implement data center operation management and improve data center availability.
O&M management
Energy efficiency management
Asset management
Capacity management
Implements a series of O&M tasks for data center infrastructure.
Operation management
Calculates and displays the power usage effectiveness (PUE) and change trend of a data center based on collected energy consumption data.
Implements standardized and process-based management of data center assets.
Through real-time monitoring, a user can learn about the space, power, cooling (SPC) usage of a data center, which facilitates quick planning and pre-warning.
Notes: O&M management: O&M management refers to a series of O&M tasks for data center infrastructure, including periodic maintenance and routine inspection of the infrastructure, fault management, system knowledge base, supplier management, and shift scheduling management. Planned preventive management effectively reduces the infrastructure failure rate. Through process-based event management, faults can be rectified as soon as possible.
Energy efficiency management: Based on collected energy consumption data, the system calculates and displays the PUE of a data center, helping users understand the real-time energy consumption composition and change trend of the data center. Based on the application of new technologies, the system deeply analyzes the energy consumption data of a data center, captures energy consumption rules of the data center, proposes reasonable energy saving measures, and supports the implementation.
Asset management: DCIM standardizes and streamlines common asset management (such as asset stocktaking, warehousing, distributing, and scrapping) in a data center.
Capacity management: monitors the SPC usage of a data center in real time to comprehensively learn about the data center. When IT services are changed, a user can quickly plan and select a proper installation position. If the system capacity usage increases, a warning is generated in advance so that capacity expansion can be planned. In addition, it can query historical capacity data, analyze capacity changes, and support capacity planning.

## Slide 22: General Control
General control is the entrance to DCIM O&M management and provides an interaction portal for O&M personnel. Generally, it includes routine management functions such as service desk, view management, and signal display.
Service desk
View management
A service desk is the entrance for O&M personnel to access various management functions. Generally, different functional modules can be displayed by O&M role.
Signal display
General control
The data center view can be displayed in multiple modes, such as 2D, 2.5D, 3D, and large screen. In addition, it supports the display of device monitoring views in multiple dimensions, such as the energy flow diagram and intra-cabinet view.
Key indicators such as data center infrastructure running information and alarm information can be displayed on a signal management page or customized based on actual O&M requirements.
Notes: Service desk: O&M management personnel can complete various O&M tasks through a service desk, such as dispatching O&M tasks, tracking task progress, processing to-dos, and releasing project bulletins.
View management: After the DCIM is configured, the general control system can display the physical topology, micro-module view, and cabinet view of a data center in multiple modes, such as 2D, 2.5D, 3D, and large screen.
Signal display: Key indicators such as data center infrastructure running and alarm information can be displayed on a signal management page or customized based on actual O&M requirements. This function can be associated with O&M tasks such as alarm notification, work order function, and report generation.

## Slide 23: Basic Services
Basic services refer to system functions provided by the DCIM system to implement management functions, including user and rights management, system management, and system service management.
Basic services
User and rights management
System management
Provides DCIM system users and rights management. Based on data center requirements, system users can be managed by level or by physical area. In addition, login authentication modes and login nodes can be controlled and managed.
System service management
The DCIM system can be managed in real time, including security management, log management, and system software management.
Manages system services provided by DCIM. These services include function licenses, network element (NE) mediations, and various authentication certificates.

## Slide 24
DCIM Physical Architecture
DCIM Logical Architecture and System Functions
DCIM System Performance and Integration

## Slide 25: DCIM System Performance
DCIM system performance refers to the capability of the system hardware to complete tasks such as collection, processing, computing, and storage.
DCIM system performance parameters include response time, management capability, processing capability, two-node cluster switchover duration, and storage capacity.
Common DCIM system performance parameters are as follows:
Response Time (s) |  | Management Capability (number of test points) |  | Two-node Cluster Switchover Duration (s) | Processing Capability | Storage Capacity
Data Collection | < 5 | Small data center | 0–10000 | < 60 | System CPU runtime usage is less than 40%. | Data can be stored for more than three years.
Device control | < 5 |  |  |  |  | 
 |  | Medium data center | 10000–20000 |  |  | 
Video surveillance refresh | < 6 |  |  |  |  | 
 |  | Large data center | > 20000 |  |  | 
Alarm generation time | < 6 |  |  |  |  | 
Notes: The control response time refers to the duration from the time when the system initiates a control signal request to the time when the corresponding device responds to the signal request.
The collection response time refers to the duration from the time when the value of a monitored object changes to the time when the collection device obtains the changed value.
The video surveillance refresh time refers to the duration from the time when the value of a monitored object changes to the time when the monitoring image in the main control center displays the change of the value.
The alarm generation time refers to the duration from the time when an alarm is generated by a monitored object to the time when the DCIM system displays the corresponding alarm status.
The shorter the two-node cluster switchover duration is, the higher the system availability is.

## Slide 26: Third-Party Integration - Introduction to Modbus Protocol
Modbus protocol:
  Modbus is the most commonly used industrial field bus protocol. It is a standard, open, and free-of-charge protocol that supports various interfaces, such as RS485 and RJ45.
  There are two types: Modbus RTU and Modbus TCP.
  Generally, Modbus refers to RTU mode, which is the most common Modbus mode.
  It supports the master/slave mode. In this mode, the host calls a device and the device answers the call.
  Analysis scope: register address, function code, read/write attribute (R/RW), data type, unit or enumerated value, proportion coefficient, value range (the value range must be confirmed for issued indicators and is optional for read-only indicators), and alarm severity (if the vendor cannot provide the alarm severity, the alarm severity needs to be customized based on experience).

## Slide 27: Third-Party Integration - Introduction to SNMP Protocol
SNMP protocol:
  Simple Network Management Protocol (SNMP) is used for network management and network device management.
  SNMP is designed to work in the TCP/IP suite.
  There are three versions: V1, V2, and V3. V1 and V2 support simple read and write, and V3 supports encryption.
  Analysis scope: signal object identifier (OID), index OID (required for table signals), read/write attribute (R/RW), data type, unit or enumerated value, proportion coefficient, value range (the value range must be confirmed for issued indicators and is optional for read-only indicators), trap alarm reporting mode, and unit.
Notes: The RS485 interface cannot use the SNMP protocol.
OID: object identifier.

## Slide 28: Common Process for Third-party Devices to Access the DCIM System
Start
Import an access package
Connect tools to devices
Connection test
Signal commissioning
Alarm commissioning
Export and update the access package
End
Signal standardization
Devices of different models from different vendors provide different northbound protocols based on their configurations. For example, Modbus and SNMP.
By defining access packages, the DCIM system can parse access protocols of devices from different vendors, convert data, and manage and monitor the devices in a unified manner.
From the perspective of customers, devices seem the same, reducing the learning cost.
From the service perspective, devices seem the same, improving service development efficiency.

## Slide 29
DCIM physical architecture
DCIM physical deployment layers
DCIM logical architecture
DCIM system functions

## Slide 30
(Multiple) Which of the following statements about the DCIM monitoring function is true?
  Through the collection function, the system can monitor various objects in real time, collect data, and upload the collected data in a unified format to the data processing layer for unified processing.
  The transmission function indicates that the collected data can be transferred between nodes in the system based on transmission policies.
  The storage function indicates that all the collected data is stored in the memory of the real-time database for system computing and historical data query.
  The processing function indicates that the collected data can be computed, analyzed, and processed based on service requirements.
Notes: Answer: ABD. The description of the storage function in option C is incorrect. Generally, a data processing system needs to perform real-time computing, which requires a high real-time performance of a storage system. The real-time database stores real-time data in the memory to ensure the real-time performance. In addition, the system needs to perform statistical analysis on historical data collected to generate data center-related reports, providing a basis for data center operation. In the system, a history database stores the collected data to the disk medium according to the time sequence for the system to invoke.

## Slide 32
Chencheng/Cwx711226
2020.07.01