## Slide 1: DCIM System Planning

## Slide 2
The slides introduce the general process of DCIM system planning, including requirement analysis, system planning, and device selection.

## Slide 3
On completion of this course, you will be able to:
  Understand main management objects of the DCIM system.
  Have a good command of main monitoring parameters and control contents of the DCIM system management objects.
  Have a good command of DCIM architecture and function requirements for data centers at different levels.
  Have a good command of principles and precautions for DCIM hardware selection.

## Slide 4
DCIM Planning Requirement Analysis
DCIM System Planning
DCIM Device Selection

## Slide 5: DCIM Planning Requirement Analysis
Different types of data centers have different requirements on the DCIM architecture and functions. The actual planning should be based on application scenarios and types.
A larger data center has more objects to manage and poses higher requirements for the DCIM system functions and performance.
DCIM should be planned based on managed objects and their management indicators.
DCIM is a data center O&M tool platform. It should be planned based on the operation and maintenance (O&M) objectives.
DCIM
requirement
analysis
Based on the availability requirements of data centers, the DCIM system planning must comply with different standards.
Industry
standards
O&M
objectives
Key
infrastructure
Data
center
scales
Data
center
types

## Slide 6: DCIM Management Objects
In the DCIM planning phase, the devices and contents to be managed by the system must be specified. Generally, common systems that need to be managed in a data center include the power supply and distribution system, cooling system, security protection system, and firefighting system.
Power supply and distribution system: generator sets, low-voltage power distribution system, automatic transfer switch (ATS), uninterruptible power system (UPS), energy storage system (ESS), UPS input and output cabinets, power distribution frames (PDFs), and power distribution units (PDUs)
Cooling system: chilled water system, precision air conditioners, humidifiers, water sensors, fresh air system, and data center temperature and humidity sensors
Security protection system: video surveillance system, access control system, and intrusion alarm system
DCIM management objects
Firefighting system: fire extinguishing controller, alarm system, and fire extinguishing system
Notes: Generally, common systems that need to be managed in a data center include the power supply and distribution system, cooling system, security protection system, and firefighting system.
Data centers of different scales, types, and management objectives must be fully considered during system planning to match different management granularities.

## Slide 7: Confirm the Basic Information About Management Objects
Confirm the communication interface type of management objects: Although there are various types of management objects, there are only two types of communication interfaces: intelligent interfaces and non-intelligent interfaces.
  Intelligent interfaces: refer to interfaces built in the monitored device for external communication. The management system only needs to communicate with the intelligent interface. Common intelligent interfaces include COM ports, FE ports, and PoE ports.
  Non-intelligent interfaces: generally include digital signal interfaces and analog signal interfaces. Currently, data centers use I/O collection modules to collect signals from these devices.
Confirm the information collection mode of management objects.
  Intelligent interfaces: Generally, a monitored management object with intelligent interfaces is directly connected through RJ45 ports to collect data. Communication protocols generally include mainstream standard protocols such as Modbus and Simple Network Management Protocol (SNMP).
  Non-intelligent interfaces: Data is collected by various sensors and collection modules, converted into standard interface information, and then sent to the management system for processing.
Determine the information to be collected from management objects.
  Before requirement analysis, confirm the communication protocol provided by device vendors, understand the meaning of each parameter, understand parameters provided in the protocol, and plan the information to be collected.
Notes: Generally, digital signals include the power distribution switch status, surge protective device (SPD) status, and fresh air unit start/stop status.
Generally, analog signals include 4–20 mA low-current signals and DC voltage signals.

## Slide 8
DCIM Planning Requirement Analysis
  Power Supply and Distribution System
  Cooling System
  Security Protection System
  Firefighting System
  Other Requirements
DCIM System Planning
DCIM Device Selection

## Slide 9: Power Supply and Distribution System
The power supply and distribution system is the power basis of a data center. To ensure continuous and stable service running, the DCIM system must monitor the running status and parameters of each node in the power supply and distribution system in real time.
Mains
Generator
High voltage distribution equipment
Transformer
Generator power distribution equipment
Low voltage distribution equipment
Input PDF
Output PDF
UPS
Battery
IT load
Power distribution architecture
Notes: The picture above shows the basic power distribution architecture of a data center.

## Slide 10: Diesel Generator
For a data center that has certain requirements on reliability and availability, one or more diesel generators are configured as the mains backup power supply. The system monitors running parameters of a generator in real time to ensure the stable running of the generator and the power supply of a data center.
Diesel generator
Running parameters
Three-phase output voltage
Three-phase output current
Output frequency
Working status
Working mode
Mains status
Fuel tank liquid level
Lubricating oil temperature
Runtime
Startup apparatus status
Fault signal
…
Control
Generator startup
Generator shutdown
Emergency shutdown
Active/standby switchover
…
Notes: Running parameters:
  Three-phase output voltage: refers to the three-phase output voltage when a generator is running.
  Three-phase output current: refers to the three-phase output current when a generator is running.
  Output frequency: refers to output frequency when the generator is running.
  Working status: running or shutdown.
  Working modes: automatic or manual.
  Mains status: The mains is faulty.
  Fuel tank liquid level: When the fuel tank liquid level of a generator decreases to a low level, the system should generate a warning or an alarm.
  Lubricant oil temperature: refers to the oil temperature when a generator is running. In addition to the oil temperature, the oil pressure is also monitored.
  Runtime: refers to the running duration after a generator is started.
  Startup apparatus: refers to the motor and battery that support the startup of a generator.
  Fault signal: indicates whether an exception occurs when the generator is running.

## Slide 11
Notes: Remote control:
  Generator startup: A generator can be started automatically or manually remotely based on operation requirements.
  Generator shutdown: A generator can be shut down automatically or manually remotely based on operation requirements.
  Emergency shutdown: A generator can be manually shut down when it is running.
  Active/standby switchover: When multiple generators are configured, the active/standby switchover can be performed automatically or manually based on operation requirements.

## Slide 12: ATS
The ATS is a device that controls the switchover between the active and standby routes of the low-voltage power distribution system. Whether the ATS operates properly is important to the normal power supply of a data center. The system must monitor the main parameters that affect the ATS operation.
ATS
Running parameters
Active/standby route voltage
Active/standby route current
Frequency of the active and standby routes
Switch status
Number of active/standby switchovers
…
Active routes
Standby routes
Notes: Active/standby route voltage: refers to the active/standby input voltage of the system.
Active/standby route current: refers to the active/standby input current.
Active/standby route frequency: refers to the primary/standby input frequency of the system.
Switch status: refers to the current position of the ATS switch.
Number of active/standby switchovers: refers to the total number of switchovers during the running of the ATS.

## Slide 13: UPS
No matter what kind of mains quality, a continuous, stable, and uninterruptible power supply cannot be ensured. Therefore, most data centers use the UPS to ensure service continuity and stability. The UPS is the core to ensure continuous power supply to IT loads in a data center. Real-time monitoring of the UPS is an important measure to ensure the UPS system reliability.
UPS
Control
Inverter startup
Inverter shutdown
Emergency shutdown
…
Running parameters
Three-phase input voltage
Three-phase input current
Input frequency
Three-phase output voltage
Three-phase output current
…
Input power
Output frequency
Output power
Bypass voltage
Bypass current
Working modes
Inverter status
Rectifier status
Battery status
Load rate

## Slide 14: Energy Storage Devices
There are two types of energy storage devices in a data center: traditional lead-acid batteries and lithium batteries. Both of them ensure continuous power supply to the UPS in the case of a mains failure.
In addition, due to the physical features of an energy storage device, a user needs to pay attention to the usage and management of the energy storage device. If the energy storage device is not properly used, its service life may decrease too fast, or even be damaged. Therefore, monitoring the energy storage device is also necessary.
Lead-acid battery
Running parameters
Voltage and current
Internal resistance
Ambient temperature
…
State of charge (SOC)
State of health (SOH)
Lithium battery
Notes: Ambient temperature: refers to the operating temperature of lead-acid batteries or lithium batteries. Generally, a temperature and humidity sensor or temperature sensor is used for monitoring.
SOC: refers to the state of charge or the remaining power of batteries. It is the ratio of the remaining capacity of a battery that has been used for a period of time or has not been used for a long time to the capacity of the battery in the fully charged state. It is usually expressed in percentage.
SOH: refers to the state of health of batteries. It is the ratio of the actual performance parameter to the nominal parameter after the battery is used for a period of time.

## Slide 15: UPS Input and Output PDFs
The UPS system is configured with input and output PDFs to form a complete UPS system.
In addition to the basic power distribution function, the UPS output PDF is generally configured with a centralized bypass switch, maintenance bypass switch, and some low-voltage protection devices. By monitoring the UPS input and output PDFs, a user can learn about the UPS input and output data in real time and understand the power supply requirements of loads in a data center.
UPS input PDF
UPS output PDF
Running parameters
Phase voltage
Line voltage
Power
Electric energy
Line current
…
Switch status
Frequency
Power distribution branch temperature
Notes: The UPS input PDF is a low-voltage PDF that distributes power to the downstream UPS. UPS output cables are connected to the UPS output PDF.

## Slide 16: Cabinet PDU
Currently, the power distribution mode of most IT cabinets in a data center is cabinet PDU power supply. The deployment is simple and power supply is convenient. The cabinet PDU directly supplies power to IT loads. Its status should be monitored by the system in real time.
Running parameters
Current
Frequency
…
Power
Voltage
Electric energy
Cabinet PDU

## Slide 17
DCIM Planning Requirement Analysis
  Power Supply and Distribution System
  Cooling System
  Security Protection System
  Firefighting System
  Other Requirements
DCIM System Planning
DCIM Device Selection

## Slide 18: Cooling System
The cooling system is the core of environment control in a data center. It ensures that IT loads work stably within a proper temperature, humidity, and cleanness range. The DCIM system monitors the operating parameters and status of main devices in each part of the cooling system in real time.
Chiller
Chilled water pump
Chilled water precision air conditioner
Cooling water pump
Cooling tower
Indoor unit of an air-cooled precision air conditioner
Chilled water tank
Outdoor unit of an air-cooled precision air conditioner
Chilled water air conditioner
Air-cooled air conditioner
Notes: This picture takes the primary pump system as an example to describe major equipment in the chilled water air conditioning system.

## Slide 19: Chilled Water System (1)
The system monitors and manages devices such as chillers, chilled water pumps, cooling towers, cooling water pumps, and plate heat exchangers in real time to ensure normal system running.
Generally, the chilled water system has an independent automatic control system. Data of the control system is integrated into the DCIM platform for unified management.
Chiller
Control
Chiller startup and shutdown
Supply and return water temperature setting
…
Running parameters
Operating voltage
Operating current
Compressor status
Compressor oil system
Drive status
Control status
…
Notes: Operating voltage and current: refer to the basic electrical parameters during the system running.
Compressor status: refers to the operating parameters and running status of the compressor in the chiller system, such as the suction and discharge pressure, operating temperature, and runtime.
Compressor oil system: refers to the lubrication and cooling system of the rotating parts of the chiller compressor.
Drive status: refers to the equipment that supports the running of the inverter compressor.
Control status: remote or local.

## Slide 20: Chilled Water System (2)
Circulates chilled and cooling water.
Chilled water circulation
Control
Chilled water pump startup and shutdown
Cooling water pump startup and shutdown
Cooling tower fan startup and shutdown
…
Running parameters
Supply and return chilled water temperatures
Chilled water pressure
Returned chilled water flow
Chilled water pump status
Chilled water pump fault
…
Cooling tower fan fault
Cooling water inlet and outlet temperatures
Cooling water pressure
Cooling water pump fault
Cooling water pump status
Cooling tower fan status
Minimum return cooling water temperature
Cooling water circulation
…
…
Notes: Chilled water pump: refers to a device that ensures the system pressure during chilled water circulation.
Supply and return chilled water temperatures: refer to the inlet and outlet water temperatures of the chiller in the chilled water circulation.
Chilled water pressure: refers to the supply and return water pressure in the chilled water circulation.
Cooling water pump: refers to a device that ensures system pressure in cooling water circulation.
Cooling water pressure: refers to the inlet and outlet water pressure in the cooling water circulation.
Cooling tower: refers to a device that absorbs system heat and discharges it into the atmosphere to lower the cooling water temperature.

## Slide 21: Chilled Water System (3)
The main functions of the fixed-pressure water refill system are as follows:
  Reduces the water pressure fluctuation caused by the water temperature change, thereby stabilizing the pressure.
  Refills the water to the pipe network system. When water leakage or drastic temperature drop occurs in the pipe network, the system refills water to the pipe network to prevent water shortage.
Water refill system
Control
Water pump startup and shutdown
Running parameters
Water pump running status
Water pump fault
Water tank liquid level
Ultra-high and ultra-low liquid level alarm
…
…

## Slide 22: Precision Air Conditioner
The precision air conditioner is a device that directly controls the temperature and humidity of a data center. Whether it works stably directly affects the IT load of the data center. Therefore, monitoring precision air conditioners is also essential.
Chilled water air conditioner
Control
Air conditioner startup and shutdown
Air conditioner startup and shutdown
Outdoor unit startup and shutdown
Running parameters
Current temperature and humidity
Humidifier status
Current temperature and humidity
Air filter status
Air-cooled air conditioner
…
Setting temperature and humidity control points
Chilled water valve opening
Supply and return water temperatures
Air filter status
Supply and return air temperature
Water leakage detection
Outdoor unit status
Fan status
Electric heater status
Compressor status
Humidifier status
Setting temperature and humidity control points
Actuator status
Water leakage detection
Fan status
Electric heater status

## Slide 23
DCIM Planning Requirement Analysis
  Power Supply and Distribution System
  Cooling System
  Security Protection System
  Firefighting System
  Other Requirements
DCIM System Planning
DCIM Device Selection

## Slide 24: Security Protection System
The video surveillance system is an electronic system or a network that uses video technologies to detect, monitor, display, and record onsite images in real time.
Video surveillance system
The security protection system consists of the video surveillance system, access control system, and intrusion alarm system.
The access control system uses modern electronic devices and software information technologies to control the access of people or objects at the entrances and exits of a data center. The control operations include allowing, rejection, recording, and alarming. The access control system is an effective measure to ensure area security and implement intelligent management.
Access control system
The intrusion alarm system is an electronic system or a network that uses sensor technologies and electronic information technologies to detect and indicate unauthorized access to a protected area, generate and process alarm information.
Intrusion alarm system

## Slide 25: Video Surveillance System Network Architecture
The video surveillance system consists of front-end equipment, transmission equipment, control equipment, and display and record equipment.
Network video recorder (NVR)
Management server
Switch
Bullet camera with pan-tilt-zoom (PTZ)
Surveillance wall
Decoder
Front-end equipment
Transmission equipment
Control equipment
Display and record equipment
Client
Bullet camera
Dome camera
Forwarding server
Network keyboard
IP network
Switch
Storage server
Notes: The video surveillance system consists of front-end equipment, transmission equipment, control equipment, and display and record equipment.
  Front-end equipment: includes one or more cameras and accompanying lenses, PTZs, shields, and decoding drivers.
  Transmission equipment: includes electrical cables and/or optical cables, and possibly wired/wireless signal modulation and demodulation equipment.
  Control equipment: includes video switchers, PTZ lens controller, keyboards, power supply, and accompanying consoles.
  Display and recording equipment: includes monitors, video recorders, and multi viewers.

## Slide 26: Video Surveillance System Monitoring Requirements
The DCIM system must monitor the video surveillance system in real time to ensure data center security.
Generally, the video surveillance system is an independent management system and is connected to the DCIM management platform in integration mode.
Video surveillance system
Running parameters
…
Real-time browsing
Equipment linkage
Remote video transmission
Alarm triggering
Recording playback
Multi-picture browsing
PTZ control
Access control

## Slide 27: Access Control System Network Architecture
The access control system generally consists of feature carriers, reading devices, locking devices, and a controller.
Card
Fingerprint
Password
Access controller
Management system
Emergency button
Door status sensor
Fingerprint and card reader with a keypad
Fingerprint reader
LED
Exit button
Notes: The access control system generally consists of feature carriers, reading devices, locking devices, and a controller.
  Feature carrier: indicates the identity and permission for entering or leaving a data center. For example, the key to a mechanical lock and an access card.
  Reading device: A device that exchanges information with a feature carrier. It reads information about identities and permissions from the feature carrier appropriately. For example, the lock insert of a mechanical lock and a card reader.
  Locking device: The access control system is practical only when it is equipped with a proper locking device. After confirming the identity and permission of the holder, a reading device allows the authorized person to enter and exit and rejects a request of the unauthorized person. For example, the magnetic lock at the access of a data center.
  Controller: refers to the core control device of the access control system. It is used for communication connection and function implementation of system components.

## Slide 28: Access Control System Monitoring Requirements
The access control system ensures the physical security of a data center and implements effective management and recording of personnel entrance and exit. Common authentication modes are password, card, fingerprint, facial recognition, and hybrid authentication.
Access control system
Running parameters
…
Door status
Historical data
Event records
Control
Remote unlocking
Remote locking
Time-limited management and control
…

## Slide 29: Intrusion Alarm System Network Architecture
The intrusion alarm system generally consists of front-end equipment, transmission equipment, operation control equipment, and display and record equipment.
Infrared sensors
Alarm button
Alarm controller
Communication transmission
Management system
Alarm beacon
Public security linkage
Notes: The intrusion alarm system generally consists of front-end equipment, transmission equipment, operation control equipment, and display and record equipment.
  Front-end equipment: The front-end detection part consists of various detectors. It is the tactile part of the intrusion alarm system. It senses the changes of physical parameters such as temperature, humidity, smell, and energy, and converts them into electrical signals that are suitable for transmission based on certain rules. For example, infrared sensors and alarm buttons.
  Transmission equipment: includes electrical cables and/or optical cables, and possibly wired/wireless signal modulation and demodulation equipment.
  Operation control equipment: generally refers to the alarm controller.
  Display and record equipment: generally refers to a device that transmits alarm information after an alarm is generated. For example, alarm beacons and monitors.

## Slide 30: Intrusion Alarm System Monitoring Requirements
The intrusion alarm system is the tactile system of a data center or an equipment room. It can detect abnormal intrusions as early as possible and report alarms in real time.
Intrusion alarm system
Running parameters
…
Front-end equipment status
Historical data
Event records
Control
System alert deployment
Alarm response
Linkage control
…

## Slide 31
DCIM Planning Requirement Analysis
  Power Supply and Distribution System
  Cooling System
  Security Protection System
  Firefighting System
  Other Requirements
DCIM System Planning
DCIM Device Selection

## Slide 32: Firefighting System
The Firefighting system of a data center is the core for monitoring and responding to fires, ensuring the safety of data center O&M personnel, and protecting equipment and property.
The system is also called the fire linkage control system. Generally, a complete firefighting system includes the fire alarm system, fire extinguishing system, smoke control system, and safety evacuation system.
  The automatic fire alarm system can implement linkage control of the fire extinguishing system, smoke control system, and safety evacuation system.
  Fire extinguishing systems are classified into gas fire extinguishing system and liquid (water) fire extinguishing system.
  The smoke control system exhausts a large amount of smoke produced by fire and prevents the smoke diffusing out of the protected zone. In this way, it ensures the smooth evacuation and safety of people in the building and create favorable conditions for firefighters to put out the fire.
  The safety evacuation system consists of fire emergency lighting and evacuation guidance lighting. When a fire occurs and the normal power supply is cut off, the safety evacuation system maintains a certain degree of lighting in important rooms or main passages of buildings. In this way, it ensures personnel can evacuate quickly so that firefighters can handle the accident timely.
Notes: The automatic fire alarm system can implement linkage control of the fire extinguishing system, smoke control system, and safety evacuation system.
Fire extinguishing systems are classified into gas fire extinguishing system and liquid (water) fire extinguishing system.
The smoke control system exhausts a large amount of smoke produced by fire and prevents the smoke diffusing out of the protected zone. In this way, it ensures the smooth evacuation and safety of people in the building and create favorable conditions for firefighters to put out the fire.
The safety evacuation system consists of fire emergency lighting and evacuation guidance lighting. When a fire occurs and the normal power supply is cut off, the safety evacuation system maintains a certain degree of lighting in important rooms or main passages of buildings. In this way, it ensures personnel can evacuate quickly so that firefighters can handle the accident timely.

## Slide 33: Firefighting System Network Architecture
Common networking architecture of the firefighting system:
Smoke detector
Heat detector
Manual pull station
Fire controller (host)
Fire alarm input signal
Fire extinguishing control
Upper-level monitoring platform
Smoke control
Alarm beacon
Fire alarm bell
Firefighting broadcast
Pressurized fan
Pressurized air supply vent
Smoke vent
Fire alarm output signal
Safety evacuation
Fire cylinders and pipe network
Startup apparatus
Fire emergency lighting
Evacuation signs
Firefighting surveillance platform
DCIM

## Slide 34: Firefighting System Monitoring Requirements
Generally, the DCIM monitors the firefighting system to obtain the running status and alarm information of the main system. The DCIM does not directly control the firefighting system and therefore does not affect the normal running of the system.
Firefighting System
Running parameters
Controller running status
Region information
Fault information
Alarm reporting time
Alarm status
…

## Slide 35
DCIM Planning Requirement Analysis
  Power Supply and Distribution System
  Cooling System
  Security Protection System
  Firefighting System
  Other Requirements
DCIM System Planning
DCIM Device Selection

## Slide 36: Other Monitoring Requirements
With the popularization of the modular concept, more data centers choose the modular deployment mode. In addition to the basic power supply and distribution, cooling, security, and firefighting systems, the data center deployed in modular mode also provides the following functions to implement intelligent management:
  IT asset information: The data center uses network data such as electronic labels to implement real-time online management of IT assets and simplify stocktaking.
  Capacity information: The data center uses the U space detection device to comprehensively manage the U space of cabinets in the data center and implement capacity management based on asset information.
  Linkage control: In addition to the default linkage control logic in the data center, a user can customize linkage rules and manage them in a unified manner based on the actual project situation or special requirements.

## Slide 37
DCIM Planning Requirement Analysis
DCIM System Planning
  DCIM Architecture Planning
  DCIM Function Selection
DCIM Device Selection

## Slide 38: DCIM Architecture Planning - Fault Tolerance
In Uptime Institute Data Center Site Infrastructure Tier Standard, the core definition of a Tier Ⅳ data center is fault tolerance. According to this requirement, the DCIM system must have the fault tolerance capability in the architecture.
Management-layer server hot backup: Multiple processing and storage servers work in hot backup mode. If the active server breaks down, the standby server takes over services timely to ensure the stable running of the DCIM system. In addition, data is backed up on multiple storage devices to ensure system operation security.
Infrastructure
Collection layer
Management layer
Fault-tolerant architecture
Display equipment
Notes: The Uptime Date Center Site Infrastructure Tier Standard requires that a Tier Ⅳ data center have multiple independent redundant devices and lines that are physically separated.
The fault tolerance and redundancy of the DCIM system are mainly reflected by the configuration of servers at the management layer.

## Slide 39: DCIM Architecture Planning - Redundancy
In Uptime Institute Data Center Site Infrastructure Tier Standard, the core definition of a Tier Ⅱ data center is redundancy. According to the requirement, the DCIM system must have the redundancy capability in the architecture.
Management-layer server redundancy: Processing and storage servers work in two-node cluster hot backup mode, and core data is backed up in redundancy mode, ensuring system architecture stability and data redundancy.
Infrastructure
Collection layer
Management layer
Redundant architecture
Display equipment

## Slide 40: DCIM Architecture Planning - Basic
In Uptime Institute Data Center Site Infrastructure Tier Standard, the core definition of a Tier Ⅰ data center is to meet basic requirements. Therefore, the system only needs to meet the basic management requirements.
Infrastructure
Collection layer
Management layer
Basic architecture
Display equipment

## Slide 41
DCIM Planning Requirement Analysis
DCIM System Planning
  DCIM Architecture Planning
  DCIM Function Selection
DCIM Device Selection

## Slide 42: DCIM Function Selection - Basic Functions
The DCIM system functions are the basis of data center O&M. Specific system functions can be selected based on the data center level and type.
The DCIM is recommended to provide the following basic functions regardless of the level and type of the data center.
Function | Remarks |  | Function | Remarks
Data collection | The system collects data of various monitored objects and adapts to various mainstream communication protocols and communication interfaces. |  | Configuration | The system provides multiple built-in device configuration (device template), page configuration (page template), and policy configuration to facilitate system deployment.
Data transmission | As for data transmission mode, the system supports query and automatic reporting. It also supports standard southbound and northbound interfaces. |  | Alarm | The system supports real-time alarm reporting, alarm analysis, and alarm notification for devices in the system.
Data processing | The system is able to process, analyze, and process various device data uploaded by the data collection layer. |  | Log | The system allows users to view and export its operation and operational logs.
Data storage | The system supports long-term data storage, export, and compression. |  | Rights management | The system supports setting multi-level rights, roles, and groups for user management.
Report | The system is able to export multiple reports in various modes. |  | System maintenance | The system supports system software functions, such as license check and software version.

## Slide 43: DCIM Function Selection - Specific Functions
In addition to basic functions, different levels, types, and service requirements of data centers affect function selection. Take the data center level as an example. Generally, the higher the level is, the higher the requirements for the DCIM system function configuration are.
The following table provides suggestions on selecting DCIM functions for data centers of different levels.
Function | Tier Ⅳ Data Center | Tier Ⅲ&Ⅱ Data Center | Tier Ⅰ Data Center
Data collection | Mandatory | Mandatory | Mandatory
Data transmission | Mandatory | Mandatory | Mandatory
Data processing | Mandatory | Mandatory | Mandatory
Data storage | Mandatory | Mandatory | Mandatory
Report | Mandatory | Mandatory | Mandatory
Configuration | Mandatory | Mandatory | Mandatory
Alarm | Mandatory | Mandatory | Mandatory
Log | Mandatory | Mandatory | Mandatory
Rights management | Mandatory | Mandatory | Mandatory
System maintenance | Mandatory | Mandatory | Mandatory
Energy consumption analysis | Mandatory | Recommended | Recommended
Trend analysis | Recommended | Recommended | Optional
Asset management | Recommended | Optional | Optional
Capacity management | Recommended | Optional | Optional
O&M management | Recommended | Optional | Optional
Two (multi) -node cluster hot backup | Mandatory | Mandatory | Optional
Notes: Mandatory: indicates that the function must be configured in this scenario.
Recommended: indicates that the function is applicable to this scenario.
Optional: indicates that the function can be chosen based on the actual situation.

## Slide 44: DCIM Performance Planning
Based on the performance required for system running, system performance is planned and determined from the following aspects: data collection interval, storage speed, refresh time, capacity, system control response time, and number of accessed clients.
This slide takes different levels of data centers as an example to describe the detailed performance planning requirements. A user can plan the performance of data centers of different scales or types based on the requirements of different levels.
Performance | Class-A Data Center | Class-B Data Center | Class-C Data Center
Single bus collection interval (s) | < 2 | < 2 | < 2
Number of refreshed test points per second | ≥ 1,0000 | ≥ 5000 | ≥ 1000
Number of concurrent events stored per minute | ≥ 2000 | ≥ 1200 | ≥ 600
Maximum number of concurrent access requests | ≥ 100 | ≥ 100 | ≥ 50

## Slide 45
DCIM Planning Requirement Analysis
DCIM System Planning
DCIM Device Selection

## Slide 46: DCIM Hardware Device Selection Principles
To achieve system unification and function integrity, DCIM system hardware is provided by software vendors or recommended partners in most cases. However, hardware must comply with certain principles no matter where the hardware comes from.
01
02
03
Basics
  The hardware must have high mechanical strength. The installation and fixing mode should have shockproof capabilities.
  Hardware selection must not affect the running of the system or other subsystems and equipment.
  Normal operating temperature: –10℃ to +50℃; humidity: 0–95% (non-condensing); altitude: ≤ 3000 m.
Reliability
  The hardware must be highly reliable (with a service life of at least five years).
  The hardware must have good electromagnetic compatibility (EMC) and the devices do not generate electromagnetic interference that affects the normal operation of the monitoring equipment.
Flexibility
  Hardware devices must be modularized to adapt to the development of modular data centers.
  The system capacity can be expanded by adding a few components (such as processors and storage disks) to the system processing and storage devices.
  The number of system communication interfaces can increase with service changes.

## Slide 47: Selection Suggestion - Power Supply and Distribution Monitoring Devices
Device Type | Suggestion | Remarks
Power detection device | Collection devices with intelligent communication interfaces are recommended. | Do not select non-intelligent devices that use analog output.
 | Devices with high data collection precision are recommended. | Electrical data is the basis of data center energy consumption analysis. The precision of this type of devices must meet certain requirements.
Switch monitoring device | Digital input collection and monitoring devices are recommended. | The switch has auxiliary contacts.
 | Digital input collection devices with high-voltage isolation or digital output devices with high-voltage input are recommended. | The switch does not have auxiliary contacts.
 | Monitoring devices with a mainstream communications port are recommended to connect to the upper-level management device. | /
 | A single device should be able to monitor the connection and disconnection status of multiway switches at the same time to reduce the number of devices in the entire system. | /
Energy storage system (ESS) collection device | Devices with mainstream communications ports are recommended to collect lead-acid battery or lithium battery parameters. | Do not use non-intelligent DC voltage and current sensors with analog output.
 | High-precision collection devices are recommended. | The voltage, current, internal resistance, and ambient temperature of batteries greatly affect the battery lifespan. If the collected data is inaccurate, the battery lifespan will be affected.
Notes: The auxiliary switch (contact) is a part of the main switch. It is configured in the power equipment such as the high-voltage or medium-voltage circuit breaker and isolation switch, and functions as the switch-off, switch-on, signal control, and interlock protection of the secondary control loop. It can also be used as the combined switch and changeover switch. The name of an auxiliary switch contains the word "auxiliary" because it is not an independent switch. It is an auxiliary carrier for breaking, connecting, and interlocking functions in the control system.

## Slide 48: Selection Suggestion - Cooling and Environment Monitoring Devices
Device Category | Suggestion | Remarks
Temperature and humidity detection device | Temperature and humidity sensors are recommended. | /
 | Sensors with liquid crystal displays (LCDs) are recommended. | /
 | Sensors with intelligent communications ports are recommended. | Do not use non-intelligent sensors with analog output.
 | High-precision sensors are recommended. Generally, the temperature error is within ±0.5℃, and the humidity error is within ±3%. | /
Water leakage detection device | If the pipe of the water system is long, the device with a water detection cable is recommended. | /
 | If the detection area is small, the regional water leakage detector (water sensor) is recommended. | /
 | Water leakage detection devices with high precision and adjustable sensitivity are recommended to reduce water intrusion risks. | /
Precision air conditioner | Devices with mainstream intelligent communication interfaces are recommended. | /
 | In the scenario with multiple devices (with redundancy configuration), devices with the teamwork control function are recommended. | The teamwork control function enables precision air conditioners to be networked and controlled, which is efficient and energy-saving.
 | Devices that can work with advanced technologies to implement intelligent management and proactive energy saving are recommended. | Keep data center devices advanced.

## Slide 49: Selection Suggestions - Security Monitoring Devices
Device Type | Suggestion | Remarks
Camera | For areas with ceilings inside the data center, semi-dome cameras are recommended. | /
 | For areas outside the data center or areas without ceilings inside the data center, bullet cameras are recommended. | /
 | For important areas or areas that require all-round surveillance, dome cameras are recommended. | /
Video server (VCN/NVR) | Video servers that comply with the international video compression standard and has multiple mainstream output interfaces are recommended. | /
 | Video servers that support functions such as real-time video viewing, historical video playback, and multi-view are recommended. | /
 | Video servers whose storage duration is longer than 30 days are recommended. | /
Access management device | Select an appropriate access controller based on the number of doors to be managed. | /
 | Access controllers with mainstream communications ports are recommended. | /
 | Access controllers and access control devices that support multiple access authentication modes are recommended. | /
Intrusion alarm device | Detectors that support all-round detection and whose detection radius is greater than or equal to three meters are recommended. | /
 | Intrusion alarm controllers that provide mainstream communication interfaces and support intrusion events, alarms, and area-based control are recommended. | /
 | Intrusion alarm controllers with the anti-sabotage function are recommended. | /

## Slide 50: Selection Suggestion - Collector and Server
Device Category | Suggestion | Remarks
Collector | An intelligent collector is recommended. | /
 | The collector should have or be able to provide sufficient AI/DI/DO communications ports. | Used to connect to non-intelligent devices for monitoring.
 | The collector should have or can be expanded to provide sufficient intelligent communication interfaces. | Used to connect to intelligent devices for monitoring.
 | The collector must have storage capacity. | When the collector is disconnected from the server, data can be stored locally. When the system is restored, the data can be used by the DCIM for supplementary collection or invoking.
 | The physical parameters of the collector must be properly set to minimize the occupation of U space in the cabinet. | /
Server | Devices from mainstream vendors or mature application vendors are recommended. | /
 | Servers that support capacity expansion (processing and storage) are recommended. | /
 | Devices with high processing capabilities and low management complexity are recommended. | /

## Slide 51
(Multiple) Which of the following are included in the security protection system of a data center?
  Firefighting system
  Video surveillance system
  Access management system
  Intrusion alarm system
(Single) Which of the following suggestions on collector selection for the DCIM system is incorrect?
  The intelligent collector is recommended.
  The collector should have or be able to provide sufficient AI/DI/DO communications ports.
  The collector should have or can be expanded to provide sufficient intelligent communication interfaces.
  The size of the collector should be the same as that of the standard server.
Notes: Answer: 1. BCD. 2. D.

## Slide 52
Main management objects of the DCIM system
Main monitoring parameters and control contents of the DCIM system management objects
DCIM architecture and function requirements for data centers at different levels
Principles and precautions for DCIM hardware selection